## Readme
Date: 8/28/2019
Notes:
LBNL developed the prototype energy models to support the evaluation of energy efficiency for data centers, e.g., the code development of ASHRAE standard 90.4.
Two types of data center models will be created: (1) small - a computer room in a building, served by CRACs, (2) large - a data center that is standalone or part of a building, served by CRAHs with a chiller plant.
Assumptions:
Definition: computer room and data center only refer to the space with IT equipment.
Size: For the computer room, 600 sf; for the data center, 6000 sf.
For each data center type, two levels of IT equipment load density are considered to represent data centers of different vintages and functions: For the computer room, 40 and 100 W/sf; for the data center, 100 and 500 W/sf. In total there are four prototype models created.
Envelope: For the computer room, adiabatic; for the datacenter: based on 90.1-2013.
HVAC: efficiency (economizer requirement too) based on 90.1-2013.
No separate consideration of variations due to vintage because it is not a determinant factor of energy use in data centers.
Team contact:
Tianzhen Hong: thong@lbl.gov
Kaiyu Sun: ksun@lbl.gov

## Computer Room
Prototype Data Center Modeling Specifications
Lawrence Berkeley National Laboratory, updated on 10-31-2016
| Item | Descriptions | Data Source
Program
| Vintage | N/A
| Location (Representing All 17 Climate Zones) | All 90.1 climate zones
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | A computer room in a building
Building Prototype
Form
| Total Floor Area (sq feet) | 600 | 1. IDC report: Special Study: Data Center of the Future 2. IDC report: U.S. Datacenter Census and Construction 2014-2018 Forecast Type: Localized data center (500-1999 sf) Average area: 573 sf
| Building shape | 30*20
| Aspect Ratio | 1:01
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | No window
Window Locations
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | One single zone | ASHRAE 90.4 Figure C.1, types of spaces that constitute a data center: Information technology equipment room, Staff office, Mechanical room, Electrical room…
| Raised floor height (feet) | 2.0-2.5 | 1.https://www.ibm.com/support/knowledgecenter/P8DEA/p8ebe/p8ebe_raisedfloors.htm 2. https://searchdatacenter.techtarget.com/answer/Data-center-raised-floors-and-ceiling-height 3. Use Best Practices to Design Data Center Facilities 4. Raised floor height is used for CFD calculation settings, not added in E+ model
| Floor to ceiling height (feet) | 14 | 1. "What is the minimum ceiling height in a data center?" 2. Data Center Components Overview
| Glazing sill height (feet) | none
Architecture
Exterior walls
| Construction | Adiabatic | This size data center is generally not standalone, but assumed to be within a building
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Adiabatic
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | none
Roof
| Construction | Adiabatic | This size data center is generally not standalone, but assumed to be within a building
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Adiabatic
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | horizontal
Window
| Dimensions | No window
Glass-Type and frame
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Operable area
Skylight
| Dimensions | No skylights
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab on the ground
| Construction | Adiabatic
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Adiabatic | This size data center is generally not standalone, but assumed to be within a building
| Thermal properties for basement walls | No insulation
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | none
| Dimensions | none
| Internal Mass | none
Air Barrier System
| Infiltration | 0 | Positive pressure
HVAC
System Type
| Heating type | none
| Cooling type | CRAC (Computer Room Air Conditioner) with DX cooling coil | 1. ASHRAE 90.1-2013: Computer rooms in buildings with a total computer room peak cooling load >3,000,000 Btu/h kW or a total computer room peak cooling load >600,000 Btu/h where the baseline HVAC system type is 7 or 8 (VAV) shall use System 11 (SZ-VAV). All other computer rooms shall use System 3 or 4 (PSZ-AC, PSZ-HP). 2.Best Practices Guide for Energy-Efficient Data Center Design: "Packaged DX air conditioners likely compose the most common type of cooling equipment for smaller data centers."
| Distribution and terminal units | UFAD
HVAC Sizing
| Air Conditioning | autosized to design day
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | SCOP 2.2/2.1/1.9 | TABLE 6.8.1-11 in ASHRAE 90.1-2013, TABLE 6.8.1K in ASHRAE 90.1-2010. 2004 and 2007 not specified, assume the same
| Heating | None | ASHRAE 90.1
HVAC Control
| Thermostat Setpoint | N/A | The control target is the supply air temperature instead of zone temperature
| Thermostat Setback | None
| Supply air temperature | Recommended => dry-bulb: 18-27°C | Thermal Guidelines for Data Processing Environment, 2nd edition. This only refer to the inlet air entering the datacom equipment.
| Supply air humidity | Controlled based on the lower limit of zone humidity (8%)
| Supply and Return Approach Temperature for ITE object in E+ | Lookup table in Sheet "" | Based on CFD simulation
| Chilled water supply temperatures | none
| Hot water supply temperatures | none
| Economizers | Air economizer depending on 90.1 requirements | ASHRAE 90.1
| Ventilation | Area Outdoor Air Rate (Ra): 0.06 cfm/ft2 V = Ra · Area | ASHRAE Ventilation Standard 62.1-2007, "Computer (not printing) under Miscellaneous Spaces"
| Demand Control Ventilation | No | ASHRAE 90.1
| Energy Recovery | No | ASHRAE 90.1
Supply Fan
| Fan Control Type | Constant speed | Title24: Constant speed if cooling capacity >= 5tons, otherwise variable speed ASHRAE 90.1-2013: variable speed fans
| Fan schedules | 24/7
| Supply Fan Total Efficiency (%) | 60% to 62% depending on the fan motor size | ASHRAE 90.1
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | None
Rated Pump Head
Pump Power
Cooling Tower
| Cooling Tower Type | None
Cooling Tower Power
Service Water Heating
| SWH type | None
Fuel type
Thermal efficiency (%)
Tank Volume (gal)
Water temperature setpoint
Water consumption
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | 1
| Schedule | Always on
| Daylighting Controls | No
| Occupancy Sensors | No
Plug load
| Average power density (W/ft2) | 40/100 | Two levels of IT loads, based on discussion with data center experts
| Schedule | See under Schedules
Occupancy
| Average people | None | ASHRAE Ventilation Standard 62.1-2007, "Computer lab under Educational Facilities"
Schedule
Misc.
Elevator
| Quantity | None
Motor type
Peak Motor Power Watts per elevator
Heat Gain to Building
Peak Fan/lights Power Watts per elevator
Motor and fan/lights Schedules
Exterior Lighting
| Peak Power | None
Schedule
References
IDC report: Special Study: Data Center of the Future
IDC report: U.S. Datacenter Census and Construction 2014-2018 Forecast
ASHRAE 90.4-2016
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
IBM data center system information. Url: http://publib.boulder.ibm.com/infocenter/flexsys/information/index.jsp?topic=%2Fcom.ibm.acc.pureflex.doc%2Fp7eek_genairconguidelines_standard.html
Michael A. Bell. Use Best Practices to Design Data Center Facilities. Url: http://www.it.northwestern.edu/bin/docs/DesignBestPractices_127434.pdf
What is the minimum ceiling height in a data center? Url: http://searchdatacenter.techtarget.com/feature/What-is-the-minimum-ceiling-height-in-a-data-center
Data Center Components Overview. Url: http://www.accu-tech.com/hs-fs/hub/54495/file-17649947-pdf/docs/dcd_overview_11-9-12.pdf
PNNL prototype models. Url: https://www.energycodes.gov/development/commercial/prototype_models
ASHRAE 90.1-2013
NREL. Best Practices Guide for Energy-Efficient Data Center Design. Url: http://www.nrel.gov/docs/fy11osti/47201.pdf
ASHRAE TC9.9. Thermal Guidelines for Data Processing Environment, 2nd edition.
ASHRAE Ventilation Standard 62.1-2007
Title 24-2016

## Data Center
Prototype Data Center Modeling Specifications
Lawrence Berkeley National Laboratory, updated on 10-31-2016
| Item | Descriptions | Data Source
Program
| Vintage | N/A
| Location | All 90.1 climate zones
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | DATA CENTER (standalone or part of a building)
Building Prototype
Form
| Total Floor Area (sq feet) | 6000 | 1. IDC report: Special Study: Data Center of the Future 2. IDC report: U.S. Datacenter Census and Construction 2014-2018 Forecast Type: Enterprise-Class Data Center 5000+ sf / 20000+ sf (Select this instead of Mid-tier Data Center because its total number of servers is larger) Average area: 13648 sf
| Building shape | 100*60
| Aspect Ratio | 1:01
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | No window
Window Locations
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | One single zone | ASHRAE 90.4 Figure C.1, types of spaces that constitute a data center: Information technology equipment room, Staff office, Mechanical room, Electrical room…
| Raised floor height (feet) | 2.0-2.5 | 1.https://www.ibm.com/support/knowledgecenter/P8DEA/p8ebe/p8ebe_raisedfloors.htm 2. https://searchdatacenter.techtarget.com/answer/Data-center-raised-floors-and-ceiling-height 3. Use Best Practices to Design Data Center Facilities 4. Raised floor height is used for CFD calculation settings, not added in E+ model
| Floor to ceiling height (feet) | 14 | 1. http://searchdatacenter.techtarget.com/feature/What-is-the-minimum-ceiling-height-in-a-data-center 2. Data Center Components Overview
| Glazing sill height (feet) | none
Architecture
Exterior walls
| Construction | Mass (pre-cast concrete panel): 8 in. Heavy-Weight Concrete + Wall Insulation + 0.5 in. gypsum board | Construction type: PNNL's CBECS Study
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | U-factor: 0.090, R-value: 11.4 c.i. | Per 90.4, envelope should follow 90.1 (2013). This shows the envelope requirements of the Climate Zone 5 as a representative.
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | none
Roof
| Construction | Built-up Roof: Roof membrane+Roof insulation+metal decking | Construction type: PNNL's CBECS Study Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Attic and Other => U-factor: 0.021, R-value: 49 | Per 90.4, envelope should follow 90.1 (2013). This shows the envelope requirements of the Climate Zone 5 as a representative.
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | horizontal
Window
| Dimensions | No window
Glass-Type and frame
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Operable area
Skylight
| Dimensions | No skylights
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab on the ground
Construction
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential, unheated; Floors, Mass | ASHRAE 90.1
| Thermal properties for basement walls | No insulation
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | none
| Dimensions | none
| Internal Mass | none
Air Barrier System
| Infiltration | 0 | Positive pressure
HVAC
System Type
| Heating type | none
| Cooling type | CRAH (Computer Room Air Handler) + Chilled water system | 1. ASHRAE 90.1-2013: Computer rooms in buildings with a total computer room peak cooling load >3,000,000 Btu/h kW or a total computer room peak cooling load >600,000 Btu/h where the baseline HVAC system type is 7 or 8 (VAV) shall use System 11 (SZ-VAV). All other computer rooms shall use System 3 or 4 (PSZ-AC, PSZ-HP). 2.Best Practices Guide for Energy-Efficient Data Center Design: "Packaged DX air conditioners likely compose the most common type of cooling equipment for smaller data centers."
| Distribution and terminal units | UFAD or Fan wall
HVAC Sizing
| Air Conditioning | autosized to design day
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | chiller COP | ASHRAE 90.1
| Heating | None | ASHRAE 90.1
HVAC Control
| Thermostat Setpoint | N/A | The control target is the supply air temperature instead of zone temperature
| Thermostat Setback | None
| Supply air temperature | Recommended => dry-bulb: 18-27°C | Thermal Guidelines for Data Processing Environment, 2nd edition. This only refer to the inlet air entering the datacom equipment.
| Supply air humidity | Controlled based on the lower limit of zone humidity (8%)
| Supply and Return Approach Temperature for ITE object in E+ | Lookup table in Sheet "" | Based on CFD simulation
| Chilled water supply temperatures | 44F
| Hot water supply temperatures | none
| Economizers | Air economizer depending on 90.1 requirements | ASHRAE 90.1
| Ventilation | Area Outdoor Air Rate (Ra): 0.06 cfm/ft2 V = Ra · Area | ASHRAE Ventilation Standard 62.1-2007, "Computer (not printing) under Miscellaneous Spaces"
| Demand Control Ventilation | No | ASHRAE 90.1
| Energy Recovery | No | ASHRAE 90.1
Supply Fan
| Fan Control Type | Variable speed fans | Title24: Constant speed if cooling capacity >= 5tons, otherwise variable speed ASHRAE 90.1-2013: variable speed fans
| Fan schedules | 24/7
| Supply Fan Total Efficiency (%) | 60% to 62% depending on the fan motor size | ASHRAE 90.1
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | Variable speed chilled water pump; Constant speed condenser water pump
| Rated Pump Head | Chilled water pump: 179 kPa Condenser water pump: 149 kPa
Pump Power
Cooling Tower
| Cooling Tower Type | Single speed cooling tower
Cooling Tower Power
Service Water Heating
| SWH type | None
Fuel type
Thermal efficiency (%)
Tank Volume (gal)
Water temperature setpoint
Water consumption
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | 1
| Schedule | Always on
| Daylighting Controls | No
| Occupancy Sensors | No
Plug load
| Average power density (W/ft2) | 100/500 | Two levels of IT loads, based on discussion with data center experts
| Schedule | See under Schedules
Occupancy
| Average people | None | ASHRAE Ventilation Standard 62.1-2007, "Computer lab under Educational Facilities"
Schedule
Misc.
Elevator
| Quantity | None
Motor type
Peak Motor Power Watts per elevator
Heat Gain to Building
Peak Fan/lights Power Watts per elevator
Motor and fan/lights Schedules
Exterior Lighting
| Peak Power | None
Schedule
References
IDC report: Special Study: Data Center of the Future
IDC report: U.S. Datacenter Census and Construction 2014-2018 Forecast
ASHRAE 90.4-2016
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
IBM data center system information. Url: http://publib.boulder.ibm.com/infocenter/flexsys/information/index.jsp?topic=%2Fcom.ibm.acc.pureflex.doc%2Fp7eek_genairconguidelines_standard.html
Michael A. Bell. Use Best Practices to Design Data Center Facilities. Url: http://www.it.northwestern.edu/bin/docs/DesignBestPractices_127434.pdf
What is the minimum ceiling height in a data center? Url: http://searchdatacenter.techtarget.com/feature/What-is-the-minimum-ceiling-height-in-a-data-center
Data Center Components Overview. Url: http://www.accu-tech.com/hs-fs/hub/54495/file-17649947-pdf/docs/dcd_overview_11-9-12.pdf
PNNL prototype models. Url: https://www.energycodes.gov/development/commercial/prototype_models
ASHRAE 90.1-2013
NREL. Best Practices Guide for Energy-Efficient Data Center Design. Url: http://www.nrel.gov/docs/fy11osti/47201.pdf
ASHRAE TC9.9. Thermal Guidelines for Data Processing Environment, 2nd edition.
ASHRAE Ventilation Standard 62.1-2007
Title 24-2016

## Schedules
Computer Equipment Schedules
Jan | 0.25
Feb | 0.5
Mar | 0.75
Apr | 1
May | 0.25
Jun | 0.5
Jul | 0.75
Aug | 1
Sep | 0.25
Oct | 0.5
Nov | 0.75
Dec | 1
Reference: ASHRAE 90.1-2013 Computer Room Equipment Schedules

## CFD assumptions
CFD simulation assumptions
| Small Data Center |  | Large Data Center |  | Reference
Room dimension | 30' * 20' (9.144m * 6.096m) |  | 100' * 60' (30.48m * 18.288m) |  | See sheets "Computer Room" and "Data Center"
Room height (feet) | 14 |  |  |  | See sheets "Computer Room" and "Data Center"
Raised floor height (feet) | 2 |  | 2.5 |  | See sheets "Computer Room" and "Data Center"
IT load density (W/ft2) | 40 | 100 | 100 | 500 | See sheets "Computer Room" and "Data Center"
Total IT load, calculated (kW) | 24 | 60 | 600 | 3000
IT rack dimensions | Height: 78.39'' (1991mm) Width: 23.62'' (600mm) Depth: 42.13'' (1070mm) |  |  |  | 42U, based on the EIA (Electronic Industries Alliance) standard
kW per rack | 4 | 5 | 15 | 20 | 1. https://lifelinedatacenters.com/data-center/data-center-power-density/ 2. http://www.datacenterjournal.com/raising-data-center-power-density/
Aisle arrangement | 7-tile pitch | 7-tile pitch | 7-tile pitch | 8-tile pitch (3-tile cold aisle) | 1. aisle pitch: measurement of row-to-row spacing between the center of adjacent cold aisles 2. https://www.server-racks.com/aisle-pitch.html 3. 2'*2' aisle
Number of rows | 2 | 4 | 10 | 10 | Data Center Projects: Establishing a Floor Plan (https://www.apc.com/salestools/VAVR-6KYMZ7/VAVR-6KYMZ7_R2_EN.pdf)
Number of racks per row, calculated | 3 | 3 | 4 | 15
Supply air temperature (°C) | 22.5 | 22.5 | 22.5 | 22.5 | Pick middle of the recommended IT inlet dry-bulb range 18-27°C according to the Thermal Guidelines for Data Processing Environment. This considers the potential temperature rise from AHU supply to IT inlet
Wall temperature (°C) | 35
Layout plan | Cold aisle on sides, hot aisles in the middle |  |  |  | Data Center Projects: Establishing a Floor Plan (https://www.apc.com/salestools/VAVR-6KYMZ7/VAVR-6KYMZ7_R2_EN.pdf)
Semi-enclosed (cold aisle) layout | Cold aisle contained to the height of the IT rack |  |  |  | https://briggsway.com/2018/06/04/hot-and-cold-aisle-containment-fans-vents-and-raised-floors/
Semi-enclosed (hot aisle) layout | Hot aisle contained to the ceiling |  |  |  | https://briggsway.com/2018/06/04/hot-and-cold-aisle-containment-fans-vents-and-raised-floors/
Fully enclosed | Combination of the two above
Scenarios to simulate
Air containment | IT load ratio | Supply air flow rate (cfm/kW) | Supply air temperature (°C)
Cold-aisle containment | 50% | 120 | 22.5
Hot-aisle containment | 100% | 200
No containment (Fully open)

## Approach Temperatures
Scenario # | Total IT load [kW] | Airflow Management - Containment |  |  | Load ratio |  | Supply air flow rate [cfm/kW] |  | Temperature [F] | [5 empty] | Temperature [C]
|  | Open | Cold | Hot | 50% | 100% | 120 | 200 | Supply air | Inlet of IT rack | Supply approach | Outlet of IT rack | Return air | Return approach | Supply approach | Return approach
1 | 24 | x |  |  | x |  | x |  | 72 | 88 | 16 | 119 | 106 | -13 | 8.8889 | -7.2222
2 | 24 | x |  |  | x |  |  | x | 72 | 86 | 14 | 104 | 91 | -13 | 7.7778 | -7.2222
3 | 24 | x |  |  |  | x | x |  | 72 | 88 | 16 | 122 | 109 | -13 | 8.8889 | -7.2222
4 | 24 | x |  |  |  | x |  | x | 72 | 85 | 13 | 106 | 94 | -12 | 7.2222 | -6.6667
5 | 24 |  | x |  | x |  | x |  | 72 | 80 | 8 | 109 | 102 | -7 | 4.4444 | -3.8889
6 | 24 |  | x |  | x |  |  | x | 72 | 79 | 7 | 96 | 89 | -7 | 3.8889 | -3.8889
7 | 24 |  | x |  |  | x | x |  | 72 | 79 | 7 | 112 | 106 | -6 | 3.8889 | -3.3333
8 | 24 |  | x |  |  | x |  | x | 72 | 77 | 5 | 98 | 92 | -6 | 2.7778 | -3.3333
9 | 24 |  |  | x | x |  | x |  | 72 | 83 | 11 | 110 | 104 | -6 | 6.1111 | -3.3333
10 | 24 |  |  | x | x |  |  | x | 72 | 81 | 9 | 97 | 91 | -6 | 5 | -3.3333
11 | 24 |  |  | x |  | x | x |  | 72 | 82 | 10 | 112 | 107 | -5 | 5.5556 | -2.7778
12 | 24 |  |  | x |  | x |  | x | 72 | 80 | 8 | 99 | 93 | -6 | 4.4444 | -3.3333
13 | 60 | x |  |  | x |  | x |  | 72 | 88 | 16 | 118 | 105 | -13 | 8.8889 | -7.2222
14 | 60 | x |  |  | x |  |  | x | 72 | 85 | 13 | 103 | 91 | -12 | 7.2222 | -6.6667
15 | 60 | x |  |  |  | x | x |  | 72 | 87 | 15 | 120 | 108 | -12 | 8.3333 | -6.6667
16 | 60 | x |  |  |  | x |  | x | 72 | 84 | 12 | 105 | 94 | -11 | 6.6667 | -6.1111
17 | 60 |  | x |  | x |  | x |  | 72 | 80 | 8 | 108 | 101 | -7 | 4.4444 | -3.8889
18 | 60 |  | x |  | x |  |  | x | 72 | 78 | 6 | 95 | 89 | -6 | 3.3333 | -3.3333
19 | 60 |  | x |  |  | x | x |  | 72 | 79 | 7 | 111 | 106 | -5 | 3.8889 | -2.7778
20 | 60 |  | x |  |  | x |  | x | 72 | 76 | 4 | 96 | 92 | -4 | 2.2222 | -2.2222
21 | 60 |  |  | x | x |  | x |  | 72 | 82 | 10 | 110 | 104 | -6 | 5.5556 | -3.3333
22 | 60 |  |  | x | x |  |  | x | 72 | 80 | 8 | 96 | 91 | -5 | 4.4444 | -2.7778
23 | 60 |  |  | x |  | x | x |  | 72 | 81 | 9 | 111 | 107 | -4 | 5 | -2.2222
24 | 60 |  |  | x |  | x |  | x | 72 | 79 | 7 | 97 | 93 | -4 | 3.8889 | -2.2222
25 | 600 | x |  |  | x |  | x |  | 72 | 87 | 15 | 118 | 105 | -13 | 8.3333 | -7.2222
26 | 600 | x |  |  | x |  |  | x | 72 | 85 | 13 | 102 | 91 | -11 | 7.2222 | -6.1111
27 | 600 | x |  |  |  | x | x |  | 72 | 86 | 14 | 119 | 108 | -11 | 7.7778 | -6.1111
28 | 600 | x |  |  |  | x |  | x | 72 | 83 | 11 | 104 | 93 | -11 | 6.1111 | -6.1111
29 | 600 |  | x |  | x |  | x |  | 72 | 79 | 7 | 108 | 101 | -7 | 3.8889 | -3.8889
30 | 600 |  | x |  | x |  |  | x | 72 | 78 | 6 | 95 | 89 | -6 | 3.3333 | -3.3333
31 | 600 |  | x |  |  | x | x |  | 72 | 78 | 6 | 110 | 105 | -5 | 3.3333 | -2.7778
32 | 600 |  | x |  |  | x |  | x | 72 | 76 | 4 | 95 | 91 | -4 | 2.2222 | -2.2222
33 | 600 |  |  | x | x |  | x |  | 72 | 81 | 9 | 109 | 104 | -5 | 5 | -2.7778
34 | 600 |  |  | x | x |  |  | x | 72 | 80 | 8 | 96 | 91 | -5 | 4.4444 | -2.7778
35 | 600 |  |  | x |  | x | x |  | 72 | 81 | 9 | 111 | 107 | -4 | 5 | -2.2222
36 | 600 |  |  | x |  | x |  | x | 72 | 79 | 7 | 96 | 92 | -4 | 3.8889 | -2.2222
37 | 3000 | x |  |  | x |  | x |  | 72 | 86 | 14 | 117 | 105 | -12 | 7.7778 | -6.6667
38 | 3000 | x |  |  | x |  |  | x | 72 | 84 | 12 | 102 | 90 | -12 | 6.6667 | -6.6667
39 | 3000 | x |  |  |  | x | x |  | 72 | 85 | 13 | 118 | 107 | -11 | 7.2222 | -6.1111
40 | 3000 | x |  |  |  | x |  | x | 72 | 82 | 10 | 103 | 93 | -10 | 5.5556 | -5.5556
41 | 3000 |  | x |  | x |  | x |  | 72 | 78 | 6 | 107 | 102 | -5 | 3.3333 | -2.7778
42 | 3000 |  | x |  | x |  |  | x | 72 | 77 | 5 | 94 | 89 | -5 | 2.7778 | -2.7778
43 | 3000 |  | x |  |  | x | x |  | 72 | 77 | 5 | 110 | 106 | -4 | 2.7778 | -2.2222
44 | 3000 |  | x |  |  | x |  | x | 72 | 75 | 3 | 94 | 91 | -3 | 1.6667 | -1.6667
45 | 3000 |  |  | x | x |  | x |  | 72 | 80 | 8 | 107 | 103 | -4 | 4.4444 | -2.2222
46 | 3000 |  |  | x | x |  |  | x | 72 | 79 | 7 | 94 | 90 | -4 | 3.8889 | -2.2222
47 | 3000 |  |  | x |  | x | x |  | 72 | 79 | 7 | 110 | 106 | -4 | 3.8889 | -2.2222
48 | 3000 |  |  | x |  | x |  | x | 72 | 78 | 6 | 95 | 92 | -3 | 3.3333 | -1.6667