## Readme
Draft for review, not to cite or circulate
2019-11-15
Notes:
ORNL is developing a prototype energy model to support the evaluation of energy efficiency for detailed large office building.
This is the initial version of the model specification, intended for review and obtaining feedback from stakeholders.
Team contact:
Piljae Im: imp1@ornl.gov
Mini Malhotra: malhotram@ornl.gov
Yeonjin Bae: baey@ornl.gov

## Building Description
Prototype Building Modeling Specifications
Oak Ridge National Laboratory, updated on June 14, 2019
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Honolulu, Hawaii (very hot, humid) Zone 1B: New Delhi, India (very hot, dry) Zone 2A: Tampa, Florida (hot, humid) Zone 2B: Tucson, Arizona (hot, dry) Zone 3A: Atlanta, Georgia (warm, humid) Zone 3B: El Paso, Texas (warm, dry) Zone 3C: San Diego, California (warm, marine) | Zone 4A: New York, New York (mixed, humid) Zone 4B: Albuquerque, New Mexico (mixed, dry) Zone 4C: Seattle, Washington (mixed, marine) Zone 5A: Buffalo, NY (cool, humid) Zone 5B: Denver, Colorado (cool, dry) Zone 5C: Port Angeles, Washington (cool, marine) | Zone 6A: Rochester, Minnesota (cold, humid) Zone 6B: Great Falls, Montana (cold, dry) Zone 7: International Falls, Minnesota (very cold) Zone 8: Fairbanks, Alaska (subarctic | Selection of representative climates based on ASHRAE Standard 169-2013
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Office
| Building Prototype | New Large Office (Detailed)
Form
| Total Floor Area (sq feet) | 498,600 (240 ft x 160 ft) |  |  | Time Saver Standards; Large Office studies (ConEd, EPRI, MEOS, NEU1(1-4), NEU2, PNL) cited in Huang et al. 1991
Building shape
| Aspect Ratio | 1.5
| Number of Floors | 12 (plus basement)
| Window Fraction (Window-to-Wall Ratio) | 40% of above-grade gross walls 37.5% of gross walls (including the below-grade walls) |  |  | When applicable, certain codes or standards may restrict the window area to lower fractions
| Window Locations | Even distribution among all four sides |  |  | PNNL's CBECS Study
| Shading Geometry | None
| Azimuth | Nnon-directional
| Thermal Zoning | Active Storage: 1.79% Atrium: 0.39% Classroom/Lecture/Training: 0.40% Conference Meeting/Multipurpose: 1.46% Corridor: 4.70% Data Center Main: 1.70% Data Center: 0.95% Dining: 1.58% Enclosed Office: 18.22% Food Prep: 0.09% Lobby: 2.38% Locker Room: 0.12% Lounge: 0.20% Electrical/Mechanical: 5.51% Open Office: 56.17% Restroom: 3.02% Stair: 1.70% Workshop: 0.10% | Basement (contains main data center) |  | Time Saver Standards; Large Office studies (ConEd, EPRI, MEOS, NEU1(1-4), NEU2, PNL) cited in Huang et al. 1992
Bottom Floor
Middle & Top Floors:
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 9
| Glazing sill height (feet) | 3 ft
Architecture
Exterior walls
| Construction | Mass (pre-cast concrete panel): 8 in. heavy-weight concrete + wall insulation + 0.5 in. gypsum board |  |  | Construction type: PNNL's CBECS Study
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane+roof insulation+metal decking |  |  | Construction type: PNNL's CBECS Study Base assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with a weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 0% |  |  | Ducker Fenestration Market Data provided by the 90.1 Envelope Subcommittee
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Basement (conditioned)
| Construction | 8" concrete wall; 6" concrete slab, 140 lbs heavy-weight aggregate
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Floors, Mass |  |  | Applicable codes or standards
| Thermal properties for basement walls | No insulation
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | One gas-fired boiler |  |  | PNNL's CBECS Study
| Cooling type | Water-source DX cooling coil with fluid cooler for datacenter in the basement and IT closets in other floors Two water-cooled centrifugal chillers for the rest of the building |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Distribution and terminal units | VAV terminal box with damper and hot-water reheating coil except (including in the basement).
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Requirements in codes or standards |  |  | Applicable codes or standards
Heating
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating |  |  | 90.1 Simulation Working Group
| Thermostat Setback | 85°F Cooling/60°F Heating
| Supply air temperature | Maximum 110F, Minimum 52F |  |  | Temperature setpoint reset may be required by codes and standards.
| Chilled water supply temperatures | 44 F
| Hot water supply temperatures | 180 F
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Pump
| Pump Type | Primary chilled water (CHW) pumps: constant speed; secondary CHW pump: variable speed; IT closet (water loop heat pump) pump: constant speed; cooling tower pump: variable speed; service hot water (SWH): constant speed; hot water (HW) pump: variable speed
| Rated Pump Head | Use the pump power assumptions as specified in 90.1 Appendix G, i.e., 22 W/gpm for chilled water pump, 19 W/gpm for hot water and condensing water pumps. For SWH pump, first estimated based on circulation flow and then adjusted based on modeled design flow. |  |  | If applicable, model inputs for other codes or standards may be different. PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | Open cooling tower with two-speed fans; two-speed fluid-cooler for data center and IT closets
| Cooling Tower Power | Autosized
Service Water Heating
| SWH type | One main water heater with storage tank
| Fuel type | Natural gas
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 300 |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | For data center and IT closet, see PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | ASHRAE Standard 62.1
| Schedule | See under Schedules
Misc.
Elevator
| Quantity |  | 12 |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0).
| Motor type |  | Traction
| Peak Motor Power Watts per elevator |  | 20370
| Heat Gain to Building |  | Exterior
| Peak Fan/lights Power Watts per elevator |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules |  | See under Schedules |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0) and Appendix DF 2007
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
ASHRAE 2013. ANSI/ASHRAE Standard 169-2013. Climatic Data for Building Design Standards. American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, Georgia. Relevant information available as Annex 1 in ASHRAE 2016
McGraw-Hill Companies, Inc. (2001). Time-Saver Standards for Building Types. New York, NY.
LBNL (1991). Huang, Joe, Akbari, H., Rainer, L. and Ritschard, R. 481 Prototypical Commercial Buildings for 20 Urban Market Areas, prepared for the Gas Research Institute, Chicago IL, also LBL-29798, Berkeley CA.
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf
Note on D14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: An updated 3D rendering of the new large office prototype was not included in the document from Dr. Piljae.
Note on E22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I assumed that the IT Closets shown on the floor plans for the Bottom and Middle/Top floors are labeled as data centers in the SketchUp model.
Note on D67: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I think this is correct, based on the report that Dr. Piljae sent (OS_LargeOffice_Distributed).

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | Zone Name (in prototype model) | Area [ft2] (with multipliers) | Conditioned [Y/N] | Volume [ft3] (with multipliers) | Multipliers | Gross Wall Area [ft2] | Window Glass Area [ft2] | Gross Wall Area [ft2] (with multipliers) | Window Glass Area [ft2] (with multipliers)
Active Storage | 8892 | 79386.6816 | 1.79%
|  |  |  | ActiveStorage_Basement_ZN | 684 | Y | 5472 | 1 | 0 | 0 | 0 | 0
|  |  |  | ActiveStorage_Bot_ZN | 684 | Y | 6159.5568 | 1 | 0 | 0 | 0 | 0
|  |  |  | ActiveStorage_Mid_ZN | 6840 | Y | 61595.568 | 10 | 0 | 0 | 0 | 0
|  |  |  | ActiveStorage_Top_ZN | 684 | Y | 6159.5568 | 1 | 0 | 0 | 0 | 0
Atrium | 1915.25 | 17247.2093 | 0.3856%
|  |  |  | Atrium_Bot_ZN | 1915.25 | Y | 17247.2093 | 1 | 432.25 | 248.8828 | 432.25 | 1915.25
Classroom/Lecture/Training | 119 | 952 | 0.396%
|  |  |  | Classroom_Basement_ZN | 119 | Y | 952 | 1 | 0 | 0 | 0 | 0
|  |  |  | Classroom_Bot_ZN | 154 | Y | 1386.8008 | 1 | 69.3401 | 39.1969 | 69.3401 | 39.1969
|  |  |  | Classroom_Mid_ZN | 1540 | Y | 13868.008 | 10 | 69.3401 | 39.1969 | 693.401 | 391.969
|  |  |  | Classroom_Top_ZN | 154 | Y | 1386.8008 | 1 | 69.3401 | 39.1969 | 69.3401 | 39.1969
Conference Meeting/Multipurpose | 7246.3854 | 64685.8192 | 1.459%
|  |  |  | ConfRoom_Basement_ZN | 566.3854 | Y | 4531.0832 | 1 | 0 | 0 | 0 | 0
|  |  |  | ConfRoom_Bot_ZN_1 | 240 | Y | 2161.248 | 1 | 108.0625 | 61.5703 | 108.0625 | 61.5703
|  |  |  | ConfRoom_Bot_ZN_2 | 280 | Y | 2521.456 | 1 | 126.0729 | 71.9766 | 126.0729 | 71.9766
|  |  |  | ConfRoom_Mid_ZN_1 | 2800 | Y | 25214.56 | 10 | 126.0729 | 71.9766 | 1260.729 | 719.766
|  |  |  | ConfRoom_Mid_ZN_2 | 2800 | Y | 25214.56 | 10 | 126.0729 | 71.9766 | 1260.729 | 719.766
|  |  |  | ConfRoom_Top_ZN_1 | 280 | Y | 2521.456 | 1 | 126.0729 | 71.9766 | 126.0729 | 71.9766
|  |  |  | ConfRoom_Top_ZN_2 | 280 | Y | 2521.456 | 1 | 126.0729 | 71.9766 | 126.0729 | 71.9766
Corridor | 23129.5003 | 207173.5223 | 4.656%
|  |  |  | Corridor_Basement_ZN_1 | 691.224 | Y | 5529.792 | 1 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Basement_ZN_2 | 280 | Y | 2240 | 1 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Basement_ZN_3 | 135.276 | Y | 1082.208 | 1 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Bot_ZN_1 | 1007.0003 | Y | 9068.2391 | 1 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Bot_ZN_2 | 820 | Y | 7384.264 | 1 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Mid_ZN_1 | 10160 | Y | 91492.832 | 10 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Mid_ZN_2 | 8200 | Y | 73842.64 | 10 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Top_ZN_1 | 1016 | Y | 9149.2832 | 1 | 0 | 0 | 0 | 0
|  |  |  | Corridor_Top_ZN_2 | 820 | Y | 7384.264 | 1 | 0 | 0 | 0 | 0
Data Center Main | 8435.6128 | 67484.9024 | 1.698%
|  |  |  | DataCenter_Basement_ZN | 8435.6128 | Y | 67484.9024 | 1 | 2123.2917 | 0 | 2123.2917 | 0
Data Center | 4704 | 42360.4608 | 0.947%
|  |  |  | DataCenter_Bot_ZN | 392 | Y | 3530.0384 | 1 | 0 | 0 | 0 | 0
|  |  |  | DataCenter_Mid_ZN | 3920 | Y | 35300.384 | 10 | 0 | 0 | 0 | 0
|  |  |  | DataCenter_Top_ZN | 392 | Y | 3530.0384 | 1 | 0 | 0 | 0 | 0
Dining | 7863.25 | 70336.4384 | 1.583%
|  |  |  | Dining_Basement_ZN | 471.25 | Y | 3770 | 1 | 0 | 0 | 0 | 0
|  |  |  | Dining_Bot_ZN | 616 | Y | 5547.2032 | 1 | 0 | 0 | 0 | 0
|  |  |  | Dining_Mid_ZN | 6160 | Y | 55472.032 | 10 | 0 | 0 | 0 | 0
|  |  |  | Dining_Top_ZN | 616 | Y | 5547.2032 | 1 | 0 | 0 | 0 | 0
Enclosed Office | 90459.3896 | 811815.3029 | 18.21%
|  |  |  | EnclosedOffice_Basement_ZN_1 | 990.1615 | Y | 7921.292 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Basement_ZN_2 | 833 | Y | 6664 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Basement_ZN_3 | 952 | Y | 7616 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Bot_1 | 952 | Y | 8572.9504 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Bot_2 | 952 | Y | 8572.9504 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Bot_3 | 960.9997 | Y | 8653.9945 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Bot_4 | 476 | Y | 4286.4752 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Bot_5 | 800 | Y | 7204.16 | 1 | 540.3125 | 310.4531 | 540.3125 | 310.4531
|  |  |  | EnclosedOffice_Bot_6 | 1097.0833 | Y | 9879.4545 | 1 | 674.0774 | 387.7412 | 674.0774 | 387.7412
|  |  |  | EnclosedOffice_Mid_1 | 9520 | Y | 85729.504 | 10 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Mid_2 | 9520 | Y | 85729.504 | 10 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Mid_3 | 9520 | Y | 85729.504 | 10 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Mid_4 | 4760 | Y | 42864.752 | 10 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Mid_5 | 9880 | Y | 88971.376 | 10 | 624.9615 | 359.3625 | 6249.615 | 3593.625
|  |  |  | EnclosedOffice_Mid_6 | 10380.208 | Y | 93475.8491 | 10 | 647.4839 | 372.3757 | 6474.839 | 3723.757
|  |  |  | EnclosedOffice_Mid_7 | 10970.833 | Y | 98794.5453 | 10 | 674.0774 | 387.7412 | 6740.774 | 3877.412
|  |  |  | EnclosedOffice_Mid_8 | 10400 | Y | 93654.08 | 10 | 648.375 | 372.8906 | 6483.75 | 3728.906
|  |  |  | EnclosedOffice_Top_1 | 952 | Y | 8572.9504 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Top_2 | 952 | Y | 8572.9504 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Top_3 | 952 | Y | 8572.9504 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Top_4 | 476 | Y | 4286.4752 | 1 | 0 | 0 | 0 | 0
|  |  |  | EnclosedOffice_Top_5 | 988 | Y | 8897.1376 | 1 | 624.9615 | 359.3625 | 624.9615 | 359.3625
|  |  |  | EnclosedOffice_Top_6 | 1038.0208 | Y | 9347.5849 | 1 | 647.4839 | 372.3757 | 647.4839 | 372.3757
|  |  |  | EnclosedOffice_Top_7 | 1097.0833 | Y | 9879.4545 | 1 | 1771.1607 | 388.1748 | 1771.1607 | 388.1748
|  |  |  | EnclosedOffice_Top_8 | 1040 | Y | 9365.408 | 1 | 648.375 | 372.8906 | 648.375 | 372.8906
Food Prep | 471.25 | 3770 | 0.09487%
|  |  |  | FoodPrep_Basement_ZN | 471.25 | Y | 3770 | 1 | 0 | 0 | 0 | 0
Lobby | 11815.3313 | 105756.0934 | 2.379%
|  |  |  | Lobby_Basement_ZN | 640 | Y | 5120 | 1 | 0 | 0 | 0 | 0
|  |  |  | Lobby_Bot_ZN_1 | 3495.3313 | Y | 31476.1574 | 1 | 788.8563 | 454.9266 | 788.8563 | 454.9266
|  |  |  | Lobby_Bot_ZN_2 | 640 | Y | 5763.328 | 1 | 0 | 0 | 0 | 0
|  |  |  | Lobby_Mid_ZN | 6400 | Y | 57633.28 | 10 | 0 | 0 | 0 | 0
|  |  |  | Lobby_Top_ZN | 640 | Y | 5763.328 | 1 | 0 | 0 | 0 | 0
Locker Room | 602.8125 | 4822.5 | 0.1214%
|  |  |  | Locker_Basement_ZN | 602.8125 | Y | 4822.5 | 1 | 0 | 0 | 0 | 0
Lounge | 987.375 | 8891.5094 | 0.1988%
|  |  |  | Lounge_Bot | 987.375 | Y | 8891.5094 | 1 | 656.0669 | 377.335 | 656.0669 | 377.335
Electrical/Mechnical | 27340.2282 | 237177.2976 | 5.504%
|  |  |  | Mechanical_Basement_ZN_1 | 8476.2282 | Y | 67809.8256 | 1 | 1669.6 | 0 | 1669.6 | 0
|  |  |  | Mechanical_Basement_ZN_2 | 504 | Y | 4032 | 1 | 0 | 0 | 0 | 0
|  |  |  | Mechanical_Bot_ZN_1 | 522 | Y | 4700.7144 | 1 | 0 | 0 | 0 | 0
|  |  |  | Mechanical_Bot_ZN_2 | 1008 | Y | 9077.2416 | 1 | 0 | 0 | 0 | 0
|  |  |  | Mechanical_Mid_ZN_1 | 5220 | Y | 47007.144 | 10 | 0 | 0 | 0 | 0
|  |  |  | Mechanical_Mid_ZN_2 | 10080 | Y | 90772.416 | 10 | 0 | 0 | 0 | 0
|  |  |  | Mechanical_Top_ZN_1 | 522 | Y | 4700.7144 | 1 | 0 | 0 | 0 | 0
|  |  |  | Mechanical_Top_ZN_2 | 1008 | Y | 9077.2416 | 1 | 0 | 0 | 0 | 0
Open Office | 278848.2193 | 2499618.4413 | 56.14%
|  |  |  | OpenOffice_Basement_ZN_1 | 3922.2724 | Y | 31378.1792 | 1 | 786.4 | 0 | 786.4 | 0
|  |  |  | OpenOffice_Basement_ZN_2 | 7483.9583 | Y | 59871.6664 | 1 | 1816.7917 | 0 | 1816.7917 | 0
|  |  |  | OpenOffice_Bot_ZN_1 | 5683.1115 | Y | 51177.5557 | 1 | 1416.5287 | 816.7226 | 1416.5287 | 816.7226
|  |  |  | OpenOffice_Bot_ZN_2 | 6686.7801 | Y | 60215.7922 | 1 | 1097.7443 | 633.3992 | 1097.7443 | 633.3992
|  |  |  | OpenOffice_Bot_ZN_3 | 6166 | Y | 55526.0632 | 1 | 1290.4464 | 744.7406 | 1290.4464 | 744.7406
|  |  |  | OpenOffice_Mid_ZN_1 | 65212.988 | Y | 587255.9995 | 10 | 1408.9024 | 813.1834 | 14089.024 | 8131.834
|  |  |  | OpenOffice_Mid_ZN_2 | 52454.167 | Y | 472360.2647 | 10 | 792.4583 | 457.0078 | 7924.583 | 4570.078
|  |  |  | OpenOffice_Mid_ZN_3 | 61660 | Y | 555260.632 | 10 | 1290.4464 | 744.7406 | 12904.464 | 7447.406
|  |  |  | OpenOffice_Mid_ZN_4 | 46951.115 | Y | 422804.1808 | 10 | 791.5672 | 456.4929 | 7915.672 | 4564.929
|  |  |  | OpenOffice_Top_ZN_1 | 6521.2988 | Y | 58725.6 | 1 | 1408.9024 | 813.1834 | 1408.9024 | 813.1834
|  |  |  | OpenOffice_Top_ZN_2 | 5245.4167 | Y | 47236.0265 | 1 | 792.4583 | 457.0078 | 792.4583 | 457.0078
|  |  |  | OpenOffice_Top_ZN_3 | 6166 | Y | 55526.0632 | 1 | 1290.4464 | 744.7406 | 1290.4464 | 744.7406
|  |  |  | OpenOffice_Top_ZN_4 | 4695.1115 | Y | 42280.4181 | 1 | 791.5672 | 456.4929 | 791.5672 | 456.4929
Restroom | 14982.5 | 133973.008 | 3.016%
|  |  |  | Restroom_Basement_ZN | 942.5 | Y | 7540 | 1 | 0 | 0 | 0 | 0
|  |  |  | Restroom_Bot_ZN | 1170 | Y | 10536.084 | 1 | 0 | 0 | 0 | 0
|  |  |  | Restroom_Mid_ZN | 11700 | Y | 105360.84 | 10 | 0 | 0 | 0 | 0
|  |  |  | Restroom_Top_ZN | 1170 | Y | 10536.084 | 1 | 0 | 0 | 0 | 0
Stair | 8424 | 75208.4352 | 1.696%
|  |  |  | Stair_Basement_ZN_1 | 324 | Y | 2592 | 1 | 0 | 0 | 0 | 0
|  |  |  | Stair_Basement_ZN_2 | 324 | Y | 2592 | 1 | 0 | 0 | 0 | 0
|  |  |  | Stair_Bot_ZN_1 | 324 | Y | 2917.6848 | 1 | 0 | 0 | 0 | 0
|  |  |  | Stair_Bot_ZN_2 | 324 | Y | 2917.6848 | 1 | 0 | 0 | 0 | 0
|  |  |  | Stair_Mid_ZN_1 | 3240 | Y | 29176.848 | 10 | 0 | 0 | 0 | 0
|  |  |  | Stair_Mid_ZN_2 | 3240 | Y | 29176.848 | 10 | 0 | 0 | 0 | 0
|  |  |  | Stair_Top_ZN_1 | 324 | Y | 2917.6848 | 1 | 0 | 0 | 0 | 0
|  |  |  | Stair_Top_ZN_2 | 324 | Y | 2917.6848 | 1 | 0 | 0 | 0 | 0
Workshop | 504 | 4032 | 0.1015%
|  |  |  | Workshop_Basement_ZN | 504 | Y | 4032 | 1 | 0 | 0 | 0 | 0
Plenum | 460235.1732 | 1840940.6928 | 0%
|  |  |  | BotFloor_Plenum | 38352.9311 | N | 153411.7244 | 1 | 1599.0208 | 0 | 1599.0208 | 0
|  |  |  | MidFloor_Plenum | 383529.311 | N | 1534117.244 | 10 | 1599.0208 | 0 | 15990.208 | 0
|  |  |  | TopFloor_Plenum | 38352.9311 | N | 153411.7244 | 1 | 1599.0208 | 0 | 1599.0208 | 0
TOTAL1 | 496740.1044 | 4434691.6218 | 100.4% | [7 empty] | 113078.5123 | 51430.1385
1. Only volume, and gross wall area include unconditioned space.

## Lighting
Lighting
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Lighting 2 [W/ft2]
|  |  |  | 2004 | 2007 | 2010 | 2013
Active Storage | 8892 | 79386.6816 | 1.79% | 0.8 | 0.8 | 0.69 | 0.63
Atrium 3 | 1915.25 | 17247.2093 | 0.3856% | 1.3 | 1.3 | 1.23 | 0.9
Classroom/Lecture/Training | 119 | 952 | 0.396% | 1.4 | 1.4 | 1.24 | 1.24
Conference Meeting/Multipurpose | 7246.3854 | 64685.8192 | 1.459% | 1.3 | 1.3 | 0.98 | 1.23
Corridor | 23129.5003 | 207173.5223 | 4.656% | 0.5 | 0.5 | 0.63 | 0.66
Data Center Main 5 | 8435.6128 | 67484.9024 | 1.698% | 1 | 1 | 0.9 | 0.82
Data Center 5 | 4704 | 42360.4608 | 0.947% | 1 | 1 | 0.9 | 0.82
Dining | 7863.25 | 70336.4384 | 1.583% | 0.9 | 0.9 | 0.65 | 0.65
Enclosed Office | 90459.3896 | 811815.3029 | 18.21% | 1.1 | 1.1 | 0.98 | 1.11
Food Prep 4 | 471.25 | 3770 | 0.09487% | 1.2 | 1.2 | 1.11 | 0.73
Lobby | 11815.3313 | 105756.0934 | 2.379% | 1.3 | 1.3 | 1.23 | 0.9
Locker Room 4 | 602.8125 | 4822.5 | 0.1214% | 1.2 | 1.2 | 1.11 | 0.73
Lounge 4 | 987.375 | 8891.5094 | 0.1988% | 1.2 | 1.2 | 1.11 | 0.73
Electrical/Mechnical | 27340.2282 | 237177.2976 | 5.504% | 1.5 | 1.5 | 0.73 | 0.42
Open Office | 278848.2193 | 2499618.4413 | 56.14% | 1.1 | 1.1 | 0.66 | 0.98
Restroom | 14982.5 | 133973.008 | 3.016% | 0.9 | 0.9 | 0.95 | 0.98
Stair | 8424 | 75208.4352 | 1.696% | 0.6 | 0.6 | 0.9 | 0.69
Workshop 4 | 504 | 4032 | 0.1015% | 1.2 | 1.2 | 1.11 | 0.73
Plenum | 460235.1732 | 1840940.6928 | 0%
TOTAL1 | 496740.1044 | 6275632.3146 | 100.4%
AREA WEIGHTED AVERAGE |  |  |  | 1.0826 | 1.0826 | 0.76777 | 0.94213
1. Only volume and gross wall area include unconditioned space.
2. This tables details the lighting power density based on applicable requirements in ASHRAE Standard 90.1 for the listed vintages (taken from the tables in the Final_Report_OS_Medium_Office_Distributed). The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Atrium" is mapped to be space type "Lobby."
4. According to the code for the updated model prototype, "Lounge," "Food Prep," "Workshop", and "Locker Room" are mapped to be space type "Breakroom."
5. The values for the "Data Center" and "Data Center Main" space types are taken from the "Space Types" tab in the OpenStudio_Standards Excel Workbook compiled by ORNL.

## Occupancy
Occupancy
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Occupancy per Area [people/1000 ft2] |  |  |  | Calculated People [ft2/person] |  |  |  | Calculated Number of People
|  |  |  | 2004 | 2007 | 2010 | 2013 | 2004 | 2007 | 2010 | 2013 | 2004 | 2007 | 2010 | 2013
Active Storage | 8892 | 79386.6816 | 1.79% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Atrium 3 | 1915.25 | 17247.2093 | 0.3856% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 19.1525 | 19.1525 | 19.1525 | 19.1525
Classroom/Lecture/Training | 119 | 952 | 0.396% | 35 | 35 | 35 | 35 | 28.5714 | 28.5714 | 28.5714 | 28.5714 | 4.165 | 4.165 | 4.165 | 4.165
Conference Meeting/Multipurpose | 7246.3854 | 64685.8192 | 1.459% | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 362.3193 | 362.3193 | 362.3193 | 362.3193
Corridor | 23129.5003 | 207173.5223 | 4.656% | 1 | 1 | 1 | 1 | 1000 | 1000 | 1000 | 1000 | 23.1295 | 23.1295 | 23.1295 | 23.1295
Data Center Main 5 | 8435.6128 | 67484.9024 | 1.698% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Data Center 5 | 4704 | 42360.4608 | 0.947% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dining | 7863.25 | 70336.4384 | 1.583% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 78.6325 | 78.6325 | 78.6325 | 78.6325
Enclosed Office | 90459.3896 | 811815.3029 | 18.21% | 4.75 | 4.75 | 4.75 | 4.75 | 210.5263 | 210.5263 | 210.5263 | 210.5263 | 429.6821 | 429.6821 | 429.6821 | 429.6821
Food Prep 4 | 471.25 | 3770 | 0.09487% | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 23.5625 | 23.5625 | 23.5625 | 23.5625
Lobby | 11815.3313 | 105756.0934 | 2.379% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 118.1533 | 118.1533 | 118.1533 | 118.1533
Locker Room 4 | 602.8125 | 4822.5 | 0.1214% | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 30.1406 | 30.1406 | 30.1406 | 30.1406
Lounge 4 | 987.375 | 8891.5094 | 0.1988% | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 49.3687 | 49.3687 | 49.3687 | 49.3687
Electrical/Mechnical | 27340.2282 | 237177.2976 | 5.504% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open Office | 278848.2193 | 2499618.4413 | 56.14% | 5.25 | 5.25 | 5.25 | 5.25 | 190.4762 | 190.4762 | 190.4762 | 190.4762 | 1463.9532 | 1463.9532 | 1463.9532 | 1463.9532
Restroom | 14982.5 | 133973.008 | 3.016% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 149.825 | 149.825 | 149.825 | 149.825
Stair | 8424 | 75208.4352 | 1.696% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Workshop 4 | 504 | 4032 | 0.1015% | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 25.2 | 25.2 | 25.2 | 25.2
Plenum | 460235.1732 | 1840940.6928 | 0%
TOTAL1 | 496740.1044 | 6275632.3146 | 100.4%
AREA WEIGHTED AVERAGE |  |  |  | 5.7212 | 5.7212 | 5.7212 | 5.7212 | 199.6972 | 199.6972 | 199.6972 | 199.6972 | 915.2566 | 915.2566 | 915.2566 | 915.2566
1. Only volume and gross wall area include unconditioned space.
2. This tables details the occupancy per area based on applicable requirements in ASHRAE Standard 62.1 for the listed vintages (taken from the tables in the Final_Report_OS_Medium_Office_Distributed). The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Atrium" is mapped to be space type "Lobby."
4. According to the code for the updated model prototype, "Lounge," "Food Prep," "Workshop", and "Locker Room" are mapped to be space type "Breakroom."
5. The values for the "Data Center" and "Data Center Main" space types are taken from the "Space Types" tab in the OpenStudio_Standards Excel Workbook compiled by ORNL.
Note on G3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These seemed off in the table in the final report about the updated large office model. The cells appeared to be shifted by one... So I just took these values from the other ASHRAE standard years (because the values for all the other years were all the same for each of the space types across the years' versions).

## Electric Equipment
Electric Equipment
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Electric Equipment per Area [W/ft2]
|  |  |  | 2004 | 2007 | 2010 | 2013
Active Storage | 8892 | 79386.6816 | 1.79% | 0 | 0 | 0 | 0
Atrium 3 | 1915.25 | 17247.2093 | 0.3856% | 0.27 | 0.07 | 0.37 | 0.07
Classroom/Lecture/Training | 119 | 952 | 0.396% | 0.93 | 0.93 | 0.93 | 0.93
Conference Meeting/Multipurpose | 7246.3854 | 64685.8192 | 1.459% | 1 | 0.37 | 0.07 | 0.37
Corridor | 23129.5003 | 207173.5223 | 4.656% | 0.29 | 0.16 | 0 | 0.16
Data Center Main 5 | 8435.6128 | 67484.9024 | 1.698% | 45 | 45 | 45 | 45
Data Center 5 | 4704 | 42360.4608 | 0.947% | 20 | 20 | 20 | 20
Dining | 7863.25 | 70336.4384 | 1.583% | 1 | 1 | 1 | 1
Enclosed Office | 90459.3896 | 811815.3029 | 18.21% | 0.87 | 0.64 | 0.71 | 0.64
Food Prep 4 | 471.25 | 3770 | 0.09487% | 5.58 | 4.46 | 0.64 | 4.46
Lobby | 11815.3313 | 105756.0934 | 2.379% | 0.27 | 0.07 | 0.37 | 0.07
Locker Room 4 | 602.8125 | 4822.5 | 0.1214% | 5.58 | 4.46 | 0.64 | 4.46
Lounge 4 | 987.375 | 8891.5094 | 0.1988% | 5.58 | 4.46 | 0.64 | 4.46
Electrical/Mechnical | 27340.2282 | 237177.2976 | 5.504% | 0.27 | 0.27 | 4.46 | 0.27
Open Office | 278848.2193 | 2499618.4413 | 56.14% | 0.96 | 0.71 | 0.16 | 0.71
Restroom | 14982.5 | 133973.008 | 3.016% | 0.27 | 0.07 | 0.27 | 0.07
Stair | 8424 | 75208.4352 | 1.696% | 0 | 0 | 0.07 | 0
Workshop 4 | 504 | 4032 | 0.1015% | 5.58 | 4.46 | 0.64 | 4.46
Plenum | 460235.1732 | 1840940.6928 | 0%
TOTAL1 | 496740.1044 | 6275632.3146 | 100.4%
AREA WEIGHTED AVERAGE |  |  |  | 1.7578 | 1.543 | 1.4616 | 1.543
1. Only volume and gross wall area include unconditioned space.
2. This tables details the electric equipment per area based the tables in the Final_Report_OS_Medium_Office_Distributed. The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Atrium" is mapped to be space type "Lobby."
4. According to the code for the updated model prototype, "Lounge," "Food Prep," "Workshop", and "Locker Room" are mapped to be space type "Breakroom."
5. The values for the "Data Center" and "Data Center Main" space types are taken from the "Space Types" tab in the OpenStudio_Standards Excel Workbook compiled by ORNL.
Note on G3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I left these values as they were pulled from Table 4, because there were several differences in each of the different vintages. However, these 2010 values seem exceptionally different (like in the Occupancy tab).

## Ventilation
Ventilation
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Ventilation per Area [ft3/min*ft2] |  |  |  | ASHRAE STANDARD Ventilation per Person [ft3/min*person]
|  |  |  | 2004 | 2007 | 2010 | 2013 | 2004 | 2007 | 2010 | 2013
Active Storage | 8892 | 79386.6816 | 1.79% | 0.05 | 0.12 | 0.06 | 0.12 | 0 | 0 | 0 | 0
Atrium 3 | 1915.25 | 17247.2093 | 0.3856% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Classroom/Lecture/Training | 119 | 952 | 0.396% | 0 | 0.12 | 0.12 | 0.12 | 16.95 | 10 | 10 | 10
Conference Meeting/Multipurpose | 7246.3854 | 64685.8192 | 1.459% | 0 | 0.06 | 0.06 | 0.06 | 20 | 5 | 0 | 5
Corridor | 23129.5003 | 207173.5223 | 4.656% | 0.05 | 0.06 | 0.12 | 0.06 | 0 | 0 | 0 | 0
Data Center Main 5 | 8435.6128 | 67484.9024 | 1.698% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Data Center 5 | 4704 | 42360.4608 | 0.947% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dining | 7863.25 | 70336.4384 | 1.583% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Enclosed Office | 90459.3896 | 811815.3029 | 18.21% | 0 | 0.06 | 0.06 | 0.06 | 20 | 5 | 5 | 5
Food Prep 4 | 471.25 | 3770 | 0.09487% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Lobby | 11815.3313 | 105756.0934 | 2.379% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Locker Room 4 | 602.8125 | 4822.5 | 0.1214% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Lounge 4 | 987.375 | 8891.5094 | 0.1988% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Electrical/Mechnical | 27340.2282 | 237177.2976 | 5.504% | 0 | 0.12 | 0.06 | 0.12 | 10 | 0 | 5 | 0
Open Office | 278848.2193 | 2499618.4413 | 56.14% | 0 | 0.06 | 0.06 | 0.06 | 20 | 5 | 0 | 5
Restroom | 14982.5 | 133973.008 | 3.016% | 0.96 | 0.06 | 0.12 | 0.06 | 0 | 5 | 0 | 0
Stair | 8424 | 75208.4352 | 1.696% | 0.05 | 0.06 | 0.06 | 0.06 | 0 | 0 | 5 | 0
Workshop 4 | 504 | 4032 | 0.1015% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Plenum | 460235.1732 | 1840940.6928 | 0%
TOTAL1 | 496740.1044 | 6275632.3146 | 100.4%
AREA WEIGHTED AVERAGE |  |  |  | 0.033026 | 0.06325 | 0.063477 | 0.06325 | 16.5081 | 4.2238 | 1.5533 | 4.073
1. Only volume and gross wall area include unconditioned space.
2. This tables details the ventilation based on applicable requirements in ASHRAE Standard 62.1 for the listed vintages (taken from the tables in the Final_Report_OS_Medium_Office_Distributed). The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Atrium" is mapped to be space type "Lobby."
4. According to the code for the updated model prototype, "Lounge," "Food Prep," "Workshop", and "Locker Room" are mapped to be space type "Breakroom."
5. The values for the "Data Center" and "Data Center Main" space types are taken from the "Space Types" tab in the OpenStudio_Standards Excel Workbook compiled by ORNL.

## Outdoor Air
Zone Summary
(90.1-2004 baseline requirements for LPD) | [9 empty] | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | Assumed Space Type | Zone Name (in prototype model) | Area [ft2] | Conditioned [Y/N] | Volume [ft3] | Multipliers | Calculated from 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
Active Storage | 8892 | 79386.6816 | 1.791% | Active Storage | [5 empty] | 0 | 0 | 533.52 | 533.52 | 0 | 0.06 | 0.06
[5 empty] | ActiveStorage_Basement_ZN | 684 | Y | 5472 | 1 |  | 0 | 533.52 | 533.52 | 0 | 0.06 | 0.06
[5 empty] | ActiveStorage_Bot_ZN | 684 | Y | 6159.5568 | 1 |  | 0 | 533.52 | 533.52 | 0 | 0.06 | 0.06
[5 empty] | ActiveStorage_Mid_ZN | 6840 | Y | 61595.568 | 10 |  | 0 | 533.52 | 533.52 | 0 | 0.06 | 0.06
[5 empty] | ActiveStorage_Top_ZN | 684 | Y | 6159.5568 | 1 |  | 0 | 533.52 | 533.52 | 0 | 0.06 | 0.06
Atrium 2 | 1915.25 | 17247.2093 | 0.3858% | Lobby | [5 empty] | 19.1525
[5 empty] | Atrium_Bot_ZN | 1915.25 | Y | 17247.2093 | 1 |  | 383.05 | 210.6775 | 210.6775 | 0.2 | 0.11 | 0.11
Classroom/Lecture/Training | 119 | 952 | 0.3962% | Classroom/Lecture/Training | [5 empty] | 4.165
[5 empty] | Classroom_Basement_ZN | 119 | Y | 952 | 1 |  | 83.3 | 27.965 | 27.965 | 0.7 | 0.235 | 0.235
[5 empty] | Classroom_Bot_ZN | 154 | Y | 1386.8008 | 1 |  | 83.3 | 27.965 | 27.965 | 0.7 | 0.235 | 0.235
[5 empty] | Classroom_Mid_ZN | 1540 | Y | 13868.008 | 10 |  | 83.3 | 27.965 | 27.965 | 0.7 | 0.235 | 0.235
[5 empty] | Classroom_Top_ZN | 154 | Y | 1386.8008 | 1 |  | 83.3 | 27.965 | 27.965 | 0.7 | 0.235 | 0.235
Conference Meeting/Multipurpose | 7246.3854 | 64685.8192 | 1.46% | Conference/Meeting/Multipurpose | [5 empty] | 362.3193
[5 empty] | ConfRoom_Basement_ZN | 566.3854 | Y | 4531.0832 | 1 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
[5 empty] | ConfRoom_Bot_ZN_1 | 240 | Y | 2161.248 | 1 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
[5 empty] | ConfRoom_Bot_ZN_2 | 280 | Y | 2521.456 | 1 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
[5 empty] | ConfRoom_Mid_ZN_1 | 2800 | Y | 25214.56 | 10 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
[5 empty] | ConfRoom_Mid_ZN_2 | 2800 | Y | 25214.56 | 10 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
[5 empty] | ConfRoom_Top_ZN_1 | 280 | Y | 2521.456 | 1 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
[5 empty] | ConfRoom_Top_ZN_2 | 280 | Y | 2521.456 | 1 |  | 7246.3854 | 2246.3795 | 2246.3795 | 1 | 0.31 | 0.31
Corridor | 23345.942 | 208905.0559 | 4.703% | Corridor/Transition | [5 empty] | 23.1295
[5 empty] | Corridor_Basement_ZN_1 | 691.224 | Y | 5529.792 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Basement_ZN_2 | 280 | Y | 2240 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Basement_ZN_3 | 351.7177 | Y | 2813.7416 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Bot_ZN_1 | 1007.0003 | Y | 9068.2391 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Bot_ZN_2 | 820 | Y | 7384.264 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Mid_ZN_1 | 10160 | Y | 91492.832 | 10 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Mid_ZN_2 | 8200 | Y | 73842.64 | 10 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Top_ZN_1 | 1016 | Y | 9149.2832 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
[5 empty] | Corridor_Top_ZN_2 | 820 | Y | 7384.264 | 1 |  | 462.59 | 1516.404 | 1516.404 | 0.019815 | 0.064954 | 0.064954
Data Center Main 4 | 8435.6128 | 67484.9024 | 1.699% | Data Center Main | [5 empty] | 0
[5 empty] | DataCenter_Basement_ZN | 8435.6128 | Y | 67484.9024 | 1 |  | 0 | 506.1368 | 506.1368 | 0 | 0.06 | 0.06
Data Center 4 | 4704 | 42360.4608 | 0.9475% | Data Center | [5 empty] | 0
[5 empty] | DataCenter_Bot_ZN | 392 | Y | 3530.0384 | 1 |  | 0 | 282.24 | 282.24 | 0 | 0.06 | 0.06
[5 empty] | DataCenter_Mid_ZN | 3920 | Y | 35300.384 | 10 |  | 0 | 282.24 | 282.24 | 0 | 0.06 | 0.06
[5 empty] | DataCenter_Top_ZN | 392 | Y | 3530.0384 | 1 |  | 0 | 282.24 | 282.24 | 0 | 0.06 | 0.06
Dining | 7863.25 | 70336.4384 | 1.584% | Dining Area | [5 empty] | 78.6325
[5 empty] | Dining_Basement_ZN | 471.25 | Y | 3770 | 1 |  | 1572.65 | 864.9575 | 864.9575 | 0.2 | 0.11 | 0.11
[5 empty] | Dining_Bot_ZN | 616 | Y | 5547.2032 | 1 |  | 1572.65 | 864.9575 | 864.9575 | 0.2 | 0.11 | 0.11
[5 empty] | Dining_Mid_ZN | 6160 | Y | 55472.032 | 10 |  | 1572.65 | 864.9575 | 864.9575 | 0.2 | 0.11 | 0.11
[5 empty] | Dining_Top_ZN | 616 | Y | 5547.2032 | 1 |  | 1572.65 | 864.9575 | 864.9575 | 0.2 | 0.11 | 0.11
Enclosed Office | 90459.3896 | 811815.3029 | 18.22% | Office-enclosed | [5 empty] | 429.6821
[5 empty] | EnclosedOffice_Basement_ZN_1 | 990.1615 | Y | 7921.292 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Basement_ZN_2 | 833 | Y | 6664 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Basement_ZN_3 | 952 | Y | 7616 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Bot_1 | 952 | Y | 8572.9504 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Bot_2 | 952 | Y | 8572.9504 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Bot_3 | 960.9997 | Y | 8653.9945 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Bot_4 | 476 | Y | 4286.4752 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Bot_5 | 800 | Y | 7204.16 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Bot_6 | 1097.0833 | Y | 9879.4545 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_1 | 9520 | Y | 85729.504 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_2 | 9520 | Y | 85729.504 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_3 | 9520 | Y | 85729.504 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_4 | 4760 | Y | 42864.752 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_5 | 9880 | Y | 88971.376 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_6 | 10380.208 | Y | 93475.8491 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_7 | 10970.833 | Y | 98794.5453 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Mid_8 | 10400 | Y | 93654.08 | 10 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_1 | 952 | Y | 8572.9504 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_2 | 952 | Y | 8572.9504 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_3 | 952 | Y | 8572.9504 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_4 | 476 | Y | 4286.4752 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_5 | 988 | Y | 8897.1376 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_6 | 1038.0208 | Y | 9347.5849 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_7 | 1097.0833 | Y | 9879.4545 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
[5 empty] | EnclosedOffice_Top_8 | 1040 | Y | 9365.408 | 1 |  | 8593.642 | 7575.9739 | 7575.9739 | 0.095 | 0.08375 | 0.08375
Food Prep 3 | 471.25 | 3770 | 0.09492% | Breakroom | [5 empty] | 23.5625
[5 empty] | FoodPrep_Basement_ZN | 471.25 | Y | 3770 | 1 |  | 471.25 | 146.0875 | 146.0875 | 1 | 0.31 | 0.31
Lobby | 11815.3313 | 105756.0934 | 2.38% | Lobby | [5 empty] | 118.1533
[5 empty] | Lobby_Basement_ZN | 640 | Y | 5120 | 1 |  | 2363.0663 | 1299.6864 | 1299.6864 | 0.2 | 0.11 | 0.11
[5 empty] | Lobby_Bot_ZN_1 | 3495.3313 | Y | 31476.1574 | 1 |  | 2363.0663 | 1299.6864 | 1299.6864 | 0.2 | 0.11 | 0.11
[5 empty] | Lobby_Bot_ZN_2 | 640 | Y | 5763.328 | 1 |  | 2363.0663 | 1299.6864 | 1299.6864 | 0.2 | 0.11 | 0.11
[5 empty] | Lobby_Mid_ZN | 6400 | Y | 57633.28 | 10 |  | 2363.0663 | 1299.6864 | 1299.6864 | 0.2 | 0.11 | 0.11
[5 empty] | Lobby_Top_ZN | 640 | Y | 5763.328 | 1 |  | 2363.0663 | 1299.6864 | 1299.6864 | 0.2 | 0.11 | 0.11
Locker Room 3 | 602.8125 | 4822.5 | 0.1214% | Breakroom | [5 empty] | 30.1406
[5 empty] | Locker_Basement_ZN | 602.8125 | Y | 4822.5 | 1 |  | 602.8125 | 186.8719 | 186.8719 | 1 | 0.31 | 0.31
Lounge 3 | 987.375 | 8891.5094 | 0.1989% | Breakroom | [5 empty] | 49.3687
[5 empty] | Lounge_Bot | 987.375 | Y | 8891.5094 | 1 |  | 987.375 | 306.0863 | 306.0863 | 1 | 0.31 | 0.31
Electrical/Mechnical | 27340.2282 | 237177.2976 | 5.507% | Electrical/Mechanical | [5 empty] | 0
[5 empty] | Mechanical_Basement_ZN_1 | 8476.2282 | Y | 67809.8256 | 1 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Basement_ZN_2 | 504 | Y | 4032 | 1 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Bot_ZN_1 | 522 | Y | 4700.7144 | 1 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Bot_ZN_2 | 1008 | Y | 9077.2416 | 1 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Mid_ZN_1 | 5220 | Y | 47007.144 | 10 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Mid_ZN_2 | 10080 | Y | 90772.416 | 10 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Top_ZN_1 | 522 | Y | 4700.7144 | 1 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
[5 empty] | Mechanical_Top_ZN_2 | 1008 | Y | 9077.2416 | 1 |  | 0 | 1640.4137 | 1640.4137 | 0 | 0.06 | 0.06
Open Office | 278848.2193 | 2499618.4413 | 56.17% | Office-open plan | [5 empty] | 1463.9532
[5 empty] | OpenOffice_Basement_ZN_1 | 3922.2724 | Y | 31378.1792 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Basement_ZN_2 | 7483.9583 | Y | 59871.6664 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Bot_ZN_1 | 5683.1115 | Y | 51177.5557 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Bot_ZN_2 | 6686.7801 | Y | 60215.7922 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Bot_ZN_3 | 6166 | Y | 55526.0632 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Mid_ZN_1 | 65212.988 | Y | 587255.9995 | 10 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Mid_ZN_2 | 52454.167 | Y | 472360.2647 | 10 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Mid_ZN_3 | 61660 | Y | 555260.632 | 10 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Mid_ZN_4 | 46951.115 | Y | 422804.1808 | 10 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Top_ZN_1 | 6521.2988 | Y | 58725.6 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Top_ZN_2 | 5245.4167 | Y | 47236.0265 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Top_ZN_3 | 6166 | Y | 55526.0632 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
[5 empty] | OpenOffice_Top_ZN_4 | 4695.1115 | Y | 42280.4181 | 1 |  | 29279.063 | 24050.6589 | 24050.6589 | 0.105 | 0.08625 | 0.08625
Restroom | 14982.5 | 133973.008 | 3.018% | Restrooms | [5 empty] | 149.825
[5 empty] | Restroom_Basement_ZN | 942.5 | Y | 7540 | 1 |  | 2996.5 | 1648.075 | 1648.075 | 0.2 | 0.11 | 0.11
[5 empty] | Restroom_Bot_ZN | 1170 | Y | 10536.084 | 1 |  | 2996.5 | 1648.075 | 1648.075 | 0.2 | 0.11 | 0.11
[5 empty] | Restroom_Mid_ZN | 11700 | Y | 105360.84 | 10 |  | 2996.5 | 1648.075 | 1648.075 | 0.2 | 0.11 | 0.11
[5 empty] | Restroom_Top_ZN | 1170 | Y | 10536.084 | 1 |  | 2996.5 | 1648.075 | 1648.075 | 0.2 | 0.11 | 0.11
Stair | 8424 | 75208.4352 | 1.697% | Stairs-active | [5 empty] | 0
[5 empty] | Stair_Basement_ZN_1 | 324 | Y | 2592 | 1 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Basement_ZN_2 | 324 | Y | 2592 | 1 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Bot_ZN_1 | 324 | Y | 2917.6848 | 1 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Bot_ZN_2 | 324 | Y | 2917.6848 | 1 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Mid_ZN_1 | 3240 | Y | 29176.848 | 10 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Mid_ZN_2 | 3240 | Y | 29176.848 | 10 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Top_ZN_1 | 324 | Y | 2917.6848 | 1 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
[5 empty] | Stair_Top_ZN_2 | 324 | Y | 2917.6848 | 1 |  | 0 | 505.44 | 505.44 | 0 | 0.06 | 0.06
Workshop 3 | 504 | 4032 | 0.1015% | Breakroom | [5 empty] | 25.2
[5 empty] | Workshop_Basement_ZN | 504 | Y | 4032 | 1 |  | 504 | 156.24 | 156.24 | 1 | 0.31 | 0.31
Plenum | 115058.7933 | 460235.1732 | 0%
[5 empty] | BotFloor_Plenum | 38352.9311 | N | 153411.7244 | 1
[5 empty] | MidFloor_Plenum | 38352.9311 | N | 153411.7244 | 1
[5 empty] | TopFloor_Plenum | 38352.9311 | N | 153411.7244 | 1
TOTAL1 | 496452.5461 | 4896658.3286 | 100.5% | [6 empty] | 2777.2842 | 2558420.1938 | 2129309.6621 | 2129309.6621 | 0.88991 | 0.69993 | 0.69993
1. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code.
2. According to the code for the updated model prototype, "Atrium" is mapped to be space type "Lobby."
3. According to the code for the updated model prototype, "Lounge," "Food Prep," "Workshop", and "Locker Room" are mapped to be space type "Breakroom."
4. The values for the "Data Center" and "Data Center Main" space types are taken from the "Space Types" tab in the OpenStudio_Standards Excel Workbook compiled by ORNL.

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Fan Schedule) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
| (°F) |  | SummerDesign | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | Sat | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
|  |  | WinterDesign | 60.08 | 60.08 | 60.08 | 60.08 | 63.68 | 67.28 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
|  |  | Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
CLGSETP_SCH | Temperature | Through 12/31 | WD | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
| (°F) |  | SummerDesign | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | Sat | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | WinterDesign | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
|  |  | Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
HTGSETP_DC_SCH | Temperature | Through 12/31 | WD | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
| (°F) |  | SummerDesign | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
|  |  | Sat | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
|  |  | WinterDesign | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
|  |  | Sun, Hol, Other | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4
CLGSETP_DC_SCH | Temperature | Through 12/31 | WD | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
| (°F) |  | SummerDesign | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
|  |  | Sat | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
|  |  | WinterDesign | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
|  |  | Sun, Hol, Other | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6 | 80.6
Cool-Supply-Air-Temp-Sch | Temperature (°F) | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
Heat-Supply-Air-Temp-Sch | Temperature (°F) | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
CW-Loop-Temp-Schedule | Temperature (°F) | Through 12/31 | All | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06
HW-Loop-Temp-Schedule | Temperature (°F) | Through 12/31 | All | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
MinOA_Sched | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(Climate Zone 1-3) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_MotorizedDamper_Sched | fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Climate Zone 4-8) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.