## Readme
Draft for review, not to cite or circulate
2019-11-15
Notes:
ORNL is developing a prototype energy model to support the evaluation of energy efficiency for detailed medium office building.
This is the initial version of the model specification, intended for review and obtaining feedback from stakeholders.
Team contact:
Piljae Im: imp1@ornl.gov
Mini Malhotra: malhotram@ornl.gov
Yeonjin Bae: baey@ornl.gov

## Building Description
Prototype Building Modeling Specifications
Oak Ridge National Laboratory, updated on June 14, 2019
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Honolulu, Hawaii (very hot, humid) Zone 1B: New Delhi, India (very hot, dry) Zone 2A: Tampa, Florida (hot, humid) Zone 2B: Tucson, Arizona (hot, dry) Zone 3A: Atlanta, Georgia (warm, humid) Zone 3B: El Paso, Texas (warm, dry) Zone 3C: San Diego, California (warm, marine) | Zone 4A: New York, New York (mixed, humid) Zone 4B: Albuquerque, New Mexico (mixed, dry) Zone 4C: Seattle, Washington (mixed, marine) Zone 5A: Buffalo, NY (cool, humid) Zone 5B: Denver, Colorado (cool, dry) Zone 5C: Port Angeles, Washington (cool, marine) | Zone 6A: Rochester, Minnesota (cold, humid) Zone 6B: Great Falls, Montana (cold, dry) Zone 7: International Falls, Minnesota (very cold) Zone 8: Fairbanks, Alaska (subarctic | Selection of representative climates based on ASHRAE Standard 169-2013
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Office
| Building Prototype | New Medium Office (Detailed)
Form
| Total Floor Area (sq feet) | 53,600 (163.8 ft x 109.2 ft)
Building shape
| Aspect Ratio | 1.5
| Number of Floors | 3
| Window Fraction (Window-to-Wall Ratio) | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) |  |  | 2003 CBECS Data and PNNL's CBECS Study 2007. When applicable, certain codes or standards may restrict the window area to lower fractions
| Window Locations | Evenly distributed along four façades
| Shading Geometry | None
| Azimuth | Non-directional
| Thermal Zoning | Active Storage: 6.86% Classroom/Lecture/Training: 0.60% Conference Meeting/Multipurpose: 5.19% Corridor: 8.96% Dining: 1.38% Enclosed Office: 18.66% Lobby: 3.70% Lounge: 1.80% Electrical/Mechanical: 3.00% Open Office: 42.55% Restroom: 3.59% Stair: 3.70% | Ground Floor:
Mid and Top Floors:
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 9 (4 ft above-ceiling plenum)
| Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass)
Architecture
Exterior walls
| Construction | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in. |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Base assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane+roof insulation+metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Base assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Roofs, Insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; vertical glazing |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 0% |  |  | Ducker Fenestration Market Data provided by the 90.1 Envelope Subcommittee
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 8" concrete slab poured directly on to the earth
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; slab-on-grade floors, unheated |  |  | Applicable codes or standards
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Additional infiltration through building entrance |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. PNNL-20026. Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Gas furnace inside the packaged air conditioning unit |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input. PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Cooling type | Packaged air conditioning unit
| Distribution and terminal units | VAV terminal box with damper and electric reheating coil
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Requirements in codes or standards Minimum equipment efficiency for air conditioners and condensing units |  |  | Applicable codes or standards
| Heating | Requirements in codes or standards Minimum equipment efficiency for warm air furnaces |  |  | Applicable codes or standards
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating
| Thermostat Setback | 80°F Cooling/60°F Heating
| Supply air temperature | Maximum 104F, Minimum 55F |  |  | Temperature setpoint reset may be required by codes and standards.
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air. |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Pump
| Pump Type | Service hot water (SWH): constant speed
| Rated Pump Head | SWH pump: first estimated based on circulation flow and then adjusted based on modeled design flow |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Efficiency | NA
Service Water Heating
| SWH type | Storage tank
| Fuel type | Natural gas
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 100 |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | ASHRAE Standard 62.1
| Schedule | See under Schedules
Misc.
Elevator
| Quantity | 2 |  |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
| Motor type | Hydraulic
| Peak Motor Power (W/elevator) | 16055
| Heat Gain to Building | Interior
| Peak Fan/lights Power (W/elevator) | 161.9 |  |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules | See under Schedules |  |  | DOE Commercial Reference Building TSD and models (V1.3_5.0) and Addendum DF to 90.1-2007
Exterior Lighting
| Peak Power (W) | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
ASHRAE 2013. ANSI/ASHRAE Standard 169-2013. Climatic Data for Building Design Standards. American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, Georgia. Relevant information available as Annex 1 in ASHRAE 2016
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | Zone Name (in prototype model) | Area [ft2] | Conditioned [Y/N] | Volume [ft3] | Multipliers | Gross Wall Area [ft2] | Window Glass Area [ft2]
Active Storage | 3677.235 | 33095.115 | 6.857%
|  |  |  | ActiveStorage_Bot_1 | 389.4948 | Y | 3505.4532 | 1 | 0 | 0
|  |  |  | ActiveStorage_Bot_2 | 346.8555 | Y | 3121.6995 | 1 | 0 | 0
|  |  |  | ActiveStorage_Bot_3 | 346.8555 | Y | 3121.6995 | 1 | 0 | 0
|  |  |  | ActiveStorage_Bot_4 | 142.5392 | Y | 1282.8528 | 1 | 0 | 0
|  |  |  | ActiveStorage_Mid_1 | 389.4948 | Y | 3505.4532 | 1 | 0 | 0
|  |  |  | ActiveStorage_Mid_2 | 346.8555 | Y | 3121.6995 | 1 | 0 | 0
|  |  |  | ActiveStorage_Mid_3 | 346.8555 | Y | 3121.6995 | 1 | 0 | 0
|  |  |  | ActiveStorage_Mid_4 | 142.5392 | Y | 1282.8528 | 1 | 0 | 0
|  |  |  | ActiveStorage_Top_1 | 389.4948 | Y | 3505.4532 | 1 | 0 | 0
|  |  |  | ActiveStorage_Top_2 | 346.8555 | Y | 3121.6995 | 1 | 0 | 0
|  |  |  | ActiveStorage_Top_3 | 346.8555 | Y | 3121.6995 | 1 | 0 | 0
|  |  |  | ActiveStorage_Top_4 | 142.5392 | Y | 1282.8528 | 1 | 0 | 0
Classroom/Lecture/Training | 320.6678 | 2886.0098 | 0.5979%
|  |  |  | ClassRoom_Bot | 320.6678 | Y | 2886.0098 | 1 | 164.7189 | 78.5861
Conference Meeting/Multipurpose | 2783.9022 | 25055.1198 | 5.191%
|  |  |  | ConfRoom_Bot_1 | 463.9837 | Y | 4175.8533 | 1 | 396 | 188.5397
|  |  |  | ConfRoom_Bot_2 | 463.9837 | Y | 4175.8533 | 1 | 396 | 188.5397
|  |  |  | ConfRoom_Mid_1 | 463.9837 | Y | 4175.8533 | 1 | 396 | 188.5397
|  |  |  | ConfRoom_Mid_2 | 463.9837 | Y | 4175.8533 | 1 | 396 | 188.5397
|  |  |  | ConfRoom_Top_1 | 463.9837 | Y | 4175.8533 | 1 | 396 | 188.5397
|  |  |  | ConfRoom_Top_2 | 463.9837 | Y | 4175.8533 | 1 | 396 | 188.5397
Corridor | 4807.6248 | 43268.6232 | 8.965%
|  |  |  | Corridor_Bot_1 | 801.2708 | Y | 7211.4372 | 1 | 0 | 0
|  |  |  | Corridor_Bot_2 | 801.2708 | Y | 7211.4372 | 1 | 0 | 0
|  |  |  | Corridor_Mid_1 | 801.2708 | Y | 7211.4372 | 1 | 0 | 0
|  |  |  | Corridor_Mid_2 | 801.2708 | Y | 7211.4372 | 1 | 0 | 0
|  |  |  | Corridor_Top_1 | 801.2708 | Y | 7211.4372 | 1 | 0 | 0
|  |  |  | Corridor_Top_2 | 801.2708 | Y | 7211.4372 | 1 | 0 | 0
Dining | 740.8669 | 6667.8018 | 1.381%
|  |  |  | Dining_Bot | 246.9556 | Y | 2222.6006 | 1 | 0 | 0
|  |  |  | Dining_Mid | 246.9556 | Y | 2222.6006 | 1 | 0 | 0
|  |  |  | Dining_Top | 246.9556 | Y | 2222.6006 | 1 | 0 | 0
Enclosed Office | 10009.3894 | 90084.5048 | 18.66%
|  |  |  | EnclosedOffice_Bot_1 | 1354.0857 | Y | 12186.7712 | 1 | 957.7494 | 458.0363
|  |  |  | EnclosedOffice_Bot_2 | 1354.0857 | Y | 12186.7712 | 1 | 957.7494 | 458.0363
|  |  |  | EnclosedOffice_Bot_3 | 488.9948 | Y | 4400.9534 | 1 | 251.109 | 119.7488
|  |  |  | EnclosedOffice_Bot_4 | 488.9948 | Y | 4400.9534 | 1 | 251.109 | 119.7488
|  |  |  | EnclosedOffice_Mid_1 | 1354.0857 | Y | 12186.7713 | 1 | 957.7494 | 458.0363
|  |  |  | EnclosedOffice_Mid_2 | 1354.0857 | Y | 12186.7713 | 1 | 957.7494 | 458.0363
|  |  |  | EnclosedOffice_Mid_3 | 453.4428 | Y | 4080.9852 | 1 | 232.9218 | 111.0232
|  |  |  | EnclosedOffice_Top_1 | 1354.0857 | Y | 12186.7713 | 1 | 957.7494 | 458.0363
|  |  |  | EnclosedOffice_Top_2 | 1354.0857 | Y | 12186.7713 | 1 | 957.7494 | 458.0363
|  |  |  | EnclosedOffice_Top_3 | 453.4428 | Y | 4080.9852 | 1 | 232.9218 | 111.0232
Lobby | 1983.5937 | 17852.3434 | 3.699%
|  |  |  | Lobby_Bot | 661.1979 | Y | 5950.7812 | 1 | 0 | 0
|  |  |  | Lobby_Mid | 661.1979 | Y | 5950.7811 | 1 | 0 | 0
|  |  |  | Lobby_Top | 661.1979 | Y | 5950.7811 | 1 | 0 | 0
Lounge | 963.9323 | 8675.3906 | 1.797%
|  |  |  | Lounge_Bot | 963.9323 | Y | 8675.3906 | 1 | 495 | 236.1835
Electrical/Mechnical | 1608.3946 | 14475.5514 | 2.999%
|  |  |  | Mechanical_Bot | 536.1315 | Y | 4825.1838 | 1 | 0 | 0
|  |  |  | Mechanical_Mid | 536.1315 | Y | 4825.1838 | 1 | 0 | 0
|  |  |  | Mechanical_Top | 536.1315 | Y | 4825.1838 | 1 | 0 | 0
Open Office | 22821.4163 | 205392.747 | 42.55%
|  |  |  | OpenOffice_Bot_1 | 2089.3165 | Y | 18803.8485 | 1 | 0 | 0
|  |  |  | OpenOffice_Bot_2 | 2281.1328 | Y | 20530.1952 | 1 | 0 | 0
|  |  |  | OpenOffice_Bot_3 | 2030.5916 | Y | 18275.3242 | 1 | 1043.0622 | 497.2768
|  |  |  | OpenOffice_Mid_1 | 2089.3165 | Y | 18803.8485 | 1 | 0 | 0
|  |  |  | OpenOffice_Mid_2 | 2281.1328 | Y | 20530.1952 | 1 | 0 | 0
|  |  |  | OpenOffice_Mid_3 | 1897.8165 | Y | 17080.3486 | 1 | 974.8593 | 464.714
|  |  |  | OpenOffice_Mid_4 | 1941.9219 | Y | 17477.2974 | 1 | 997.2189 | 475.3893
|  |  |  | OpenOffice_Top_1 | 2089.3165 | Y | 18803.8485 | 1 | 0 | 0
|  |  |  | OpenOffice_Top_2 | 2281.1328 | Y | 20530.1952 | 1 | 0 | 0
|  |  |  | OpenOffice_Top_3 | 1897.8165 | Y | 17080.3486 | 1 | 974.8593 | 464.714
|  |  |  | OpenOffice_Top_4 | 1941.9219 | Y | 17477.2971 | 1 | 997.2189 | 475.3893
Restroom | 1928.0079 | 17352.0708 | 3.595%
|  |  |  | Restroom_Bot | 642.6693 | Y | 5784.0234 | 1 | 0 | 0
|  |  |  | Restroom_Mid | 642.6693 | Y | 5784.0237 | 1 | 0 | 0
|  |  |  | Restroom_Top | 642.6693 | Y | 5784.0237 | 1 | 0 | 0
Stair | 1983.0937 | 17847.8436 | 3.698%
|  |  |  | Stair_Bot_1 | 330.5156 | Y | 2974.6406 | 1 | 0 | 0
|  |  |  | Stair_Bot_2 | 330.5156 | Y | 2974.6406 | 1 | 0 | 0
|  |  |  | Stair_Mid_1 | 330.5156 | Y | 2974.6406 | 1 | 0 | 0
|  |  |  | Stair_Mid_2 | 330.5156 | Y | 2974.6406 | 1 | 0 | 0
|  |  |  | Stair_Top_1 | 330.5156 | Y | 2974.6406 | 1 | 0 | 0
|  |  |  | Stair_Top_2 | 330.5156 | Y | 2974.6406 | 1 | 0 | 0
Plenum | 53628.1414 | 214512.5655 | 0%
|  |  |  | FirstFloor_Plenum | 17876.0471 | N | 71504.1885 | 1 | 2183.5726 | 0
|  |  |  | MidFloor_Plenum | 17876.0471 | N | 71504.1885 | 1 | 2183.5726 | 0
|  |  |  | TopFloor_Plenum | 17876.0471 | N | 71504.1885 | 1 | 2183.5726 | 0
TOTAL1 | 53628.1246 | 697165.6867 | 100% | [5 empty] | 21288.2133 | 7033.253
1. Only volume, and gross wall area include unconditioned space.

## Lighting
Lighting
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Lighting 2 [W/ft2]
|  |  |  | 2004 | 2007 | 2010 | 2013
Active Storage | 3677.235 | 33095.115 | 6.857% | 0.8 | 0.8 | 0.63 | 0.63
Classroom/Lecture/Training | 320.6678 | 2886.0098 | 0.5979% | 1.4 | 1.4 | 1.24 | 1.24
Conference Meeting/Multipurpose | 2783.9022 | 25055.1198 | 5.191% | 1.3 | 1.3 | 1.23 | 1.23
Corridor | 4807.6248 | 43268.6232 | 8.965% | 0.5 | 0.5 | 0.66 | 0.66
Dining | 740.8669 | 6667.8018 | 1.381% | 0.9 | 0.9 | 0.65 | 0.65
Enclosed Office | 10009.3894 | 90084.5048 | 18.66% | 1.1 | 1.1 | 1.11 | 1.11
Lobby | 1983.5937 | 17852.3434 | 3.699% | 1.3 | 1.3 | 0.9 | 0.9
Lounge 3 | 963.9323 | 8675.3906 | 1.797% | 1.3 | 1.3 | 0.9 | 0.9
Electrical/Mechnical | 1608.3946 | 14475.5514 | 2.999% | 1.5 | 1.5 | 0.95 | 0.42
Open Office | 22821.4163 | 205392.747 | 42.55% | 1.1 | 1.1 | 0.98 | 0.98
Restroom | 1928.0079 | 17352.0708 | 3.595% | 1.1 | 0.9 | 0.98 | 0.98
Stair | 1983.0937 | 17847.8436 | 3.698% | 0.6 | 0.6 | 0.69 | 0.69
Plenum | 53628.1414 | 214512.5655 | 0%
TOTAL1 | 53628.1246 | 697165.6867 | 100%
AREA WEIGHTED AVERAGE |  |  |  | 1.0396 | 1.0324 | 0.94553 | 0.92963
1. Only volume and gross wall area include unconditioned space.
2. This tables details the lighting power density based on applicable requirements in ASHRAE Standard 90.1 for the listed vintages (taken from the tables in the Final_Report_OS_Medium_Office_Distributed). The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Lounge" is mapped to be space type "Lobby."
Note on E11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Mapped as "BreakRoom" in the large office model. Can assume the same here? However, i don't have the ASHRAE 90.1 standards for each of the vintages... So I will just refer to the comment below. Reply: When I use the same values as were used for "Lobby," I get the same weighted average values (except for the one for 2004, which is off by 0.01) that are listed in the the tables in the final detailed report. Thus, this is what I am currentlty using in this scorecard report.

## Occupancy
Occupancy
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Occupancy per Area [people/1000 ft2] |  |  |  | Calculated People [ft2/person] |  |  |  | Calculated Number of People
|  |  |  | 2004 | 2007 | 2010 | 2013 | 2004 | 2007 | 2010 | 2013 | 2004 | 2007 | 2010 | 2013
Active Storage | 3677.235 | 33095.115 | 6.857% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Classroom/Lecture/Training | 320.6678 | 2886.0098 | 0.5979% | 35 | 35 | 35 | 35 | 28.5714 | 28.5714 | 28.5714 | 28.5714 | 11.2234 | 11.2234 | 11.2234 | 11.2234
Conference Meeting/Multipurpose | 2783.9022 | 25055.1198 | 5.191% | 50 | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 139.1951 | 139.1951 | 139.1951 | 139.1951
Corridor | 4807.6248 | 43268.6232 | 8.965% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dining | 740.8669 | 6667.8018 | 1.381% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 7.4087 | 7.4087 | 7.4087 | 7.4087
Enclosed Office | 10009.3894 | 90084.5048 | 18.66% | 4.75 | 4.75 | 4.75 | 4.75 | 210.5263 | 210.5263 | 210.5263 | 210.5263 | 47.5446 | 47.5446 | 47.5446 | 47.5446
Lobby | 1983.5937 | 17852.3434 | 3.699% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 19.8359 | 19.8359 | 19.8359 | 19.8359
Lounge 3 | 963.9323 | 8675.3906 | 1.797% | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 9.6393 | 9.6393 | 9.6393 | 9.6393
Electrical/Mechnical | 1608.3946 | 14475.5514 | 2.999% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open Office | 22821.4163 | 205392.747 | 42.55% | 5.25 | 5.25 | 5.25 | 5.25 | 190.4762 | 190.4762 | 190.4762 | 190.4762 | 119.8124 | 119.8124 | 119.8124 | 119.8124
Restroom | 1928.0079 | 17352.0708 | 3.595% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stair | 1983.0937 | 17847.8436 | 3.698% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plenum | 53628.1414 | 214512.5655 | 0%
TOTAL1 | 53628.1246 | 697165.6867 | 100%
AREA WEIGHTED AVERAGE |  |  |  | ASHRAE STANDARD Occupancy per Area [people/1000 ft2] 2004: 6.6133; ASHRAE STANDARD Occupancy per Area [people/1000 ft2] 2007: 6.6133; ASHRAE STANDARD Occupancy per Area [people/1000 ft2] 2010: 6.6133; ASHRAE STANDARD Occupancy per Area [people/1000 ft2] 2013: 6.6133
1. Only volume and gross wall area include unconditioned space.
2. This tables details the occupancy per area based on applicable requirements in ASHRAE Standard 62.1 for the listed vintages (taken from the tables in the Final_Report_OS_Medium_Office_Distributed). The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Lounge" is mapped to be space type "Lobby."

## Electric Equipment
Electric Equipment
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Electric Equipment per Area [W/ft2]
|  |  |  | 2004 | 2007 | 2010 | 2013
Active Storage | 3677.235 | 33095.115 | 6.857% | 0 | 0 | 0 | 0
Classroom/Lecture/Training | 320.6678 | 2886.0098 | 0.5979% | 0.929 | 0.929 | 0.929 | 0.929
Conference Meeting/Multipurpose | 2783.9022 | 25055.1198 | 5.191% | 1 | 1 | 1 | 1
Corridor | 4807.6248 | 43268.6232 | 8.965% | 0.29 | 0.29 | 0.29 | 0.29
Dining | 740.8669 | 6667.8018 | 1.381% | 1 | 1 | 1 | 1
Enclosed Office | 10009.3894 | 90084.5048 | 18.66% | 0.87 | 0.87 | 0.87 | 0.87
Lobby | 1983.5937 | 17852.3434 | 3.699% | 0.27 | 0.27 | 0.27 | 0.27
Lounge 3 | 963.9323 | 8675.3906 | 1.797% | 0.27 | 0.27 | 0.27 | 0.27
Electrical/Mechnical | 1608.3946 | 14475.5514 | 2.999% | 0.27 | 0.27 | 0.27 | 0.27
Open Office | 22821.4163 | 205392.747 | 42.55% | 0.96 | 0.96 | 0.96 | 0.96
Restroom | 1928.0079 | 17352.0708 | 3.595% | 0.27 | 0.27 | 0.27 | 0.27
Stair | 1983.0937 | 17847.8436 | 3.698% | 0 | 0 | 0 | 0
Plenum | 53628.1414 | 214512.5655 | 0%
TOTAL1 | 53628.1246 | 697165.6867 | 100%
AREA WEIGHTED AVERAGE |  |  |  | 0.70083 | 0.70083 | 0.70083 | 0.70083
1. Only volume and gross wall area include unconditioned space.
2. This tables details the electric equipment per area based the tables in the Final_Report_OS_Medium_Office_Distributed. The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Lounge" is mapped to be space type "Lobby."

## Ventilation
Ventilation
Zone Type | Zone Area Total [ft2] | Zone Volume Total [ft3] | Area Percentage [%] | ASHRAE STANDARD Ventilation per Area [ft3/min*ft2] |  |  |  | ASHRAE STANDARD Ventilation per Person [ft3/min*person]
|  |  |  | 2004 | 2007 | 2010 | 2013 | 2004 | 2007 | 2010 | 2013
Active Storage | 3677.235 | 33095.115 | 6.857% | 0.15 | 0.12 | 0.12 | 0.12 | 0 | 0 | 0 | 0
Classroom/Lecture/Training | 320.6678 | 2886.0098 | 0.5979% | 0 | 0.12 | 0.12 | 0.12 | 16.95 | 10 | 10 | 10
Conference Meeting/Multipurpose | 2783.9022 | 25055.1198 | 5.191% | 0 | 0.06 | 0.06 | 0.06 | 20 | 5 | 5 | 5
Corridor | 4807.6248 | 43268.6232 | 8.965% | 0.05 | 0.06 | 0.06 | 0.06 | 0 | 0 | 0 | 0
Dining | 740.8669 | 6667.8018 | 1.381% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Enclosed Office | 10009.3894 | 90084.5048 | 18.66% | 0 | 0.06 | 0.06 | 0.06 | 20 | 5 | 5 | 5
Lobby | 1983.5937 | 17852.3434 | 3.699% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Lounge 3 | 963.9323 | 8675.3906 | 1.797% | 0 | 0.06 | 0.06 | 0.06 | 15 | 5 | 5 | 5
Electrical/Mechnical | 1608.3946 | 14475.5514 | 2.999% | 0.15 | 0.12 | 0.12 | 0.12 | 0 | 0 | 0 | 0
Open Office | 22821.4163 | 205392.747 | 42.55% | 0 | 0.06 | 0.06 | 0.06 | 20 | 5 | 5 | 5
Restroom | 1928.0079 | 17352.0708 | 3.595% | 0.05 | 0.06 | 0.06 | 0.06 | 0 | 0 | 0 | 0
Stair | 1983.0937 | 17847.8436 | 3.698% | 0.05 | 0.06 | 0.06 | 0.06 | 0 | 0 | 0 | 0
Plenum | 53628.1414 | 214512.5655 | 0%
TOTAL1 | 53628.1246 | 697165.6867 | 100%
AREA WEIGHTED AVERAGE |  |  |  | ASHRAE STANDARD Ventilation per Area [ft3/min*ft2] 2004: 0.022913; ASHRAE STANDARD Ventilation per Area [ft3/min*ft2] 2007: 0.066272; ASHRAE STANDARD Ventilation per Area [ft3/min*ft2] 2010: 0.066272; ASHRAE STANDARD Ventilation per Area [ft3/min*ft2] 2013: 0.066272
1. Only volume and gross wall area include unconditioned space.
2. This tables details the ventilation based on applicable requirements in ASHRAE Standard 62.1 for the listed vintages (taken from the tables in the Final_Report_OS_Medium_Office_Distributed). The actual inputs for the models are based on applicable codes and standards.
3. According to the code for the updated model prototype, "Lounge" is mapped to be space type "Lobby."

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multipliers | Assumed Space Type | Calculated from 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
Active Storage | 3677.235 | 1 | Active Storage | 0 | 0 | 220.6341 | 220.6341 | 0 | 0.06 | 0.06
Classroom/Lecture/Training | 320.6678 | 1 | Classroom/Lecture/Training | 11.2234 | 224.4674 | 75.3569 | 75.3569 | 0.7 | 0.235 | 0.235
Conference Meeting/Multipurpose | 2783.9022 | 1 | Conference/Meeting/Multipurpose | 139.1951 | 2783.9022 | 863.0097 | 863.0097 | 1 | 0.31 | 0.31
Corridor | 4807.6248 | 1 | Corridor/Transition | 0 | 0 | 288.4575 | 288.4575 | 0 | 0.06 | 0.06
Dining | 740.8669 | 1 | Dining Area | 7.4087 | 148.1734 | 81.4954 | 81.4954 | 0.2 | 0.11 | 0.11
Enclosed Office | 10009.3894 | 1 | Office-enclosed | 47.5446 | 950.892 | 838.2864 | 838.2864 | 0.095 | 0.08375 | 0.08375
Lobby | 1983.5937 | 1 | Lobby | 19.8359 | 396.7187 | 218.1953 | 218.1953 | 0.2 | 0.11 | 0.11
Lounge 2 | 963.9323 | 1 | Lobby | 9.6393 | 192.7865 | 106.0326 | 106.0326 | 0.2 | 0.11 | 0.11
Electrical/Mechnical | 1608.3946 | 1 | Electrical/Mechanical | 0 | 0 | 96.5037 | 96.5037 | 0 | 0.06 | 0.06
Open Office | 22821.4163 | 1 | Office-open plan | 119.8124 | 2396.2487 | 1968.3472 | 1968.3472 | 0.105 | 0.08625 | 0.08625
Restroom | 1928.0079 | 1 | Restrooms | 0 | 0 | 115.6805 | 115.6805 | 0 | 0.06 | 0.06
Stair | 1983.0937 | 1 | Stairs-active | 0 | 0 | 118.9856 | 118.9856 | 0 | 0.06 | 0.06
Plenum | 53628.1414 | 1
TOTAL | 53628.1246 |  |  | 354.6594 | 7093.1889 | 4990.9847 | 4990.9847 | 0.13227 | 0.093067 | 0.093067
1. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code.
2. According to the code for the updated model prototype, "Lounge" is mapped to be space type "Lobby."
Residential single bedroom apartment
Corridors (public spaces)
Office space
Note on D4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Types taken from ASHRAE 90.1 (2004), Table 9.6.1. These types also match those in the OpenStudio_Standards workbook (with the exceptions of Lounge/Recreation and Classroom/Lecture/Training, which are not included in the OpenStudio_Standards workbook).
Note on I18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I copied this formula from the original PNNL medium office scorecard; however, I just wanted to make a note that the formula for these totals for the small and medium offices differ from that in the large office scorecard. The formula in the large office seems to account for multipliers that do NOT equal 1.

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Saturday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exterior Lighting Schedule
BLDG_EXTERIOR_LIGHT | Fraction | Through 12/31 | All Days | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(AstronomicalClock control)
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
INFIL_SCH_PNNL | Fraction | Through 12/31 | Weekday, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Saturday, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Schedules
HVACOperationSchd | On/off | Through 12/31 | Weekday, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Fan Schedule) |  |  | Saturday, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | Weekday | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
|  |  | Saturday | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
CLGSETP_SCH | Temperature | Through 12/31 | Weekday | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
|  |  | Saturday | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
|  |  | Sun, Hol, Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
| (°C) |  | SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
HTGSETP_SCH | Temperature | Through 12/31 | Weekday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
| (°F) |  | Saturday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | WinterDesign | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 63.68 | 67.28 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
CLGSETP_SCH | Temperature | Through 12/31 | Weekday | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
| (°F) |  | Saturday | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
|  |  | SummerDesign | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.