## Readme
Draft for review, not to cite or circulate
Original: 1/14/2020; Last Updated: 1/15/2020
Notes:
LBNL is developing a prototype energy model to support the evaluation of energy efficiency for mixed-use tall buildings.
This is the initial version of the model specification, intended for review and obtaining feedback from stakeholders.
LBNL team contact:
Tianzhen Hong: thong@lbl.gov
Kaiyu Sun: ksun@lbl.gov
Sang Hoon Lee
Wanni Zhang

## Building Description
Prototype Tall Buildings Modeling Specifications
Lawrence Berkeley National Laboratory, updated on 1-14-2020
| Item | Descriptions (Tall Buildings, >100m) | Descriptions (SuperTall Buildings, >300m) | Data Sources | Questions/To confirm
Program
| Vintage | 2004, 2007, 2010, 2013, 2016
| Location | All 90.1 climate zones |  | Selection of representative climates based on Briggs et al. (2003)
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Depending on the actual layout of building functions
| Building Prototype | Mixed-use Tall and SuperTall Buildings (retail + office + residential + hotel) |  | <ASHRAE Design Guide for tall, supertall and megatall building systems> P1: "A modern-day description is “mixed use”, where at ground level there could be retail and food and beverage space. Possibly, the first section of the building could be commercial (offices), the second section could be residential, and the lucrative high-level section could be a hotel."
Form
| Total Floor Area (sq feet) | 780,000 ( 152.8ft x 130.9ft x (38+1) stories) | 1,460,000 ( 152.8ft x 130.9ft x (72+1) stories) | NYC citygml dataset, median floor area is 20,130 ≈ 20,000 ft2
| Building shape | Rectangular
| Aspect Ratio | 1.168 |  | NYC citygml dataset
| Number of Floors | 38 (plus basement): 2 retails + 18 offices + 9 residential + 9 hotels The floor distribution is flexible in OpenStudio measure | 72 (plus basement): 3 retails + 34 offices + 1 skylobby + 17 residential + 17 hotels The floor distribution is flexible in OpenStudio measure | - Total number of floors from Global Tall Building Database of the CTBUH. - ASHRAE TC9.12: 2~4 retails, then 50% offices, 50% residential - Skylobby is an intermediate interchange floor for switching elevators, which is unique for supertall buildings - Elevator machine room (conditioned) is on top of the roof
| Window Fraction (Window-to-Wall Ratio) | 60% of above-grade gross walls |  | <ASHRAE Design Guide for tall, supertall and megatall building systems> Table 3.2-3.4 | Table B.2 shows 60%. Which should go with?
| Window Locations | Evenly distributed along four façades
| Shading Geometry | None
| Azimuth | Long side faces South and North
| Thermal Zoning | Varies with floor function (different zoning for office, retail, residential and hotel) | Varies with floor function (different zoning for office, retail, residential and hotel) | <ASHRAE Design Guide for tall, supertall and megatall building systems> P16: "On larger floor plates (i.e., those with areas greater than 20,000 gross square feet, it is a core that often will take less than approximately 15% to 20% of the total floor area of a given floor." | Assuming this core area percentage decreases when the total floor area increases, with 20,000 ft2 being the lower limit, we adopt a higher percentage, 20%. | Update: 15% for tall building, 20% for super tall as it needs more elevator hoistway | Update: 15% for both tall and supertall, but add sky lobby so no need for extra elevator rolls
| Floor to floor height (feet) | Retail: floor-floor 16ft; floor-ceiling 14ft Office and other types: 11.5ft Basement: floor-floor 16ft, no plenum | Retail and basement: floor-floor 16ft; floor-ceiling 14ft Office and other types: 13.8ft Basement: floor-floor 16ft, no plenum | Global Tall Building Database of the CTBUH TC9.12, for super tall buildings: - Retail: floor-floor 16ft; floor-ceiling 14ft - Office: 13.8ft (other floor types are the same because the floor functions may vary with tenants)
| Floor to ceiling height (feet) | 9 | 10.5 | <ASHRAE Design Guide for tall, supertall and megatall building systems> P19 and P207 (window height)
| Glazing sill height (feet) | 0
Architecture
Exterior walls
| Construction | Steel-frame walls (2X4 16 in o.c.) 0.4 in. stucco+5/8 in. gypsum board + wall Insulation+5/8 in. gypsum board |  | Approximation construction structure. U-value will refer to 90.1
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Mass |  | Applicable codes or standards (ASHRAE 90.1)
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up roof: Roof membrane+roof insulation+metal decking
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Roofs - Insulation entirely above deck |  | Applicable codes or standards (ASHRAE 90.1)
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Double-pane window. Hypothetical window with weighted U-factor and SHGC |  |  | Specific type of double-skin façade and modeling methods
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; Vertical glazing - Metal framing (curtainwall/storefront) |  | Applicable codes or standards (ASHRAE 90.1)
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 0% |  |  | Is natural ventilation common in double-skin façade/tall and supertall?
Skylight
| Dimensions | No skylights
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Basement (conditioned) |  |  | Parking floor?
| Construction | 8" concrete wall; 6" concrete slab, 140 lbs heavy-weight aggregate
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Floors - Mass |  | Applicable codes or standards (ASHRAE 90.1)
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration (cfm/ft2 exterior wall) | - Perimeter zones Infiltration peak value (No infiltration for core zones), cfm/ft2 exterior wall: ASHRAE 90.1 2004: 0.202, 2007: 0.202, 2010: 0.112, 2013: 0.112, 2016: 0.112 - Peak: when fans turn off, at peak: when fans turn on, 25% of peak - Adjusted by wind |  | PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Centralized hot-water gas boilers |  | Number of boilers will be determined after sizing simulation. Minimum of 2 for redundancy | Number of boilers? And redundancy?
| Cooling type | Centralized water-cooled chillers |  | Number of chillers will be determined after sizing simulation. Minimum of 2 for redundancy | Number of chillers? And redundancy?
| Distribution and terminal units | - Office and retail: Floor-by-Floor AHU with VAV terminal - Residential and hotel: fan coil + DOAS (to each room), VAV for hotel common areas - DOAS supplying neutral outdoor air to each AHU, or subcooled to remove additional moisture, depending on humidity requirement |  | <ASHRAE Design Guide for tall, supertall and megatall building systems> P95:"Experience on large projects shows that the maximum number of floors from the central mechanical equipment room is limited to approximately 20 to 24 floors"; P86:"Typically, the outdoor air for the system is provided by an air-handling unit located on the roof or in a central mechanical equipment room that provides outdoor air to the unit on each floor by means of a vertical duct riser, in a shaft that is routed to each of the multiple air-conditioning local floor-by-floor air-handling units."
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Efficiency varies by design cooling capacity Requirements in codes or standards |  | Applicable codes or standards (ASHRAE 90.1)
| Heating | Boiler efficiency varies by climate location and design heating capacity Requirements in codes or standards
HVAC Control
| Thermostat Setpoint | Varies with space types. See under Space Type Summary Example: Offices: 75°F Cooling/70°F Heating Apartments: 75°F Cooling/70°F Heating |  | DOE prototype models
| Thermostat Setback | Varies with space types. See under Space Type Summary Example: Offices: 85°F Cooling/60°F Heating Apartments: No setback |  | DOE prototype models
| Supply air temperature | Cooling 55F, Heating maximum 110F |  | - <ASHRAE Design Guide for tall, supertall and megatall building systems> P130 - DOE Prototype large office model
| Chilled water supply temperatures | 44F |  | DOE Prototype large office model
| Hot water supply temperatures | 180 F |  | DOE Prototype large office model
| Economizers - air side | None |  | <ASHRAE Design Guide for tall, supertall and megatall building systems> P86:"This system, regardless of geographic location and the outdoor air temperature and humidity variation during the year, usually operates on minimum outdoor air during all periods of occupancy." | Economizer - air and water
| Economizers - water side | Requirements in codes or standards. When required, interpose a flat plate heat exchanger between the chilled water and condenser water circuits |  | - Applicable codes or standards (ASHRAE 90.1) - <HVAC Design Guide for High Rise Tall Buildings> P46: With the air-conditioning supply systems operating on minimum outdoor air at all times, the code-mandated economizer requirement can be achieved, in periods of low wet-bulb temperature, through the use of the condenser water from the cooling tower as a means of cooling the chilled water that is supplied to the floor-by-floor air-conditioning units. This can be done by either of two approaches. The first would be to interpose a flat plate heat exchanger between the chilled water and condenser water and condenser water circuits. The second would be through injecting the condenser water directly into the chilled water system after passing the condenser water through a bypass sand filter to remove any potential fouling material from the condenser water.
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code Varies with space types See under Outdoor Air |  | ASHRAE standard 62.1
| Demand Control Ventilation | Requirements in codes or standards
| Energy Recovery | Requirements in codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Exhaust Fan
| Fan schedules | See under Schedules Applicable to specific space types (e.g. laundry, dining)
| Exhaust airflow rate | Applicable to hotel kitchen and laundry See under Outdoor Air |  | ASHRAE standard 62.1
| Fan Total Efficiency (%) | 55% |  | - PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Fan Pressure Drop | 0.5 in. w.c.
Pump
| Pump Type | Primary chilled water (CHW) pumps: constant speed; Secondary CHW pump: variable speed; Condensing Water (CW) pump: variable speed; Hot water (HW) pump: variable speed |  | ASHRAE 90.1 Appendix G
| Rated Pump Head | Use the pump power assumptions as specified in 90.1 Appendix G, i.e., 22 W/gpm for chilled water pump, 19 W/gpm for hot water and condensing water pumps. |  | - ASHRAE 90.1 Appendix G - PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | Open cooling tower with variable-speed fan
| Cooling Tower Power | autosized |  |  | Number of cooling towers? And redundancy?
Service Water Heating
| SWH type | Multizone distribution with multiple pumps One water heater and one pump per 100ft |  | - <ASHRAE Design Guide for tall, supertall and megatall building systems> P149-150 "Typically, to avoid excessive pressure, buildings taller than 100 ft (30 m) require multiple water distribution zones." - PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models | Pump distribution and pump head assumptions
| Fuel type | Natural gas
| Thermal efficiency (%) | Requirements in codes or standards |  | Applicable codes or standards
| Pump Type | Constant speed
| Rated Pump Head | Refers to large office, large hotel and highrise aparment - 10ft of water (29890Pa)
| Tank Volume (gal) | 300 |  | PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140F |  | PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | See under Space Type Summary Requirements in codes or standards |  | ASHRAE 90.1 Table 9.5.1 Lighting Power Densities using the Building Area Method
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | Varies with space types See under Space Type Summary
| Schedule | See under Schedules
Occupancy
| Average people | Varies with space types See under Space Type Summary
| Schedule | See under Schedules
Misc.
Elevator
| Quantity | 17 Allocation=> retail: 1; office: 8; residential: 4; hotel: 4 | 32 Allocation=> retail: 1; office: 15; residential: 8; hotel: 8 | - <ASHRAE Design Guide for tall, supertall and megatall building systems> P132: rule of thumb, one elevator for each 40,000 to 50,000 gross ft2, use 45,000ft here. - For supertall and megatall, sky lobby approach is used. At least one elevator machine room will be in the middle of the building. - Number of elevators applied to each function type will be allocated according to their number of floors
| HVAC equipment | packaged air-cooled DX unit | packaged air-cooled DX unit | <ASHRAE Design Guide for tall supertall and megatall building systems> P140-141. Size should be autosized based on elevator power. DX unit may require 10-15 tons or more in a single EMR
| Motor type | Traction
| Peak Motor Power Watts per elevator (kW) | 28.3 | 44.6 | Schindler product brochure. For tall building: 180m rise, 1150kg load (machine room dimensions: 2500x4350x2600mm); For super tall, 300m rise (super tall can reach most 600 meter), 1150kg load (machine room dimensions: 2700x4505x4200mm). 15% of the motor power is dissipated as heat | 2 rolls of elevator => big machine room width = single machine room width*2 (supertall: 4.505*2) | machine room width of Tall used dimension of two elevator roll + elevator lobby
| Heat Gain to Building | Interior, 15% of motor power |  | Schindler product brochure
| Peak Fan/lights Power Watts per elevator (W) | 161.9 |  | DOE Prototype Models (Large Office, Large Hotel and Highrise Apartment)
| Motor and fan/lights Schedules | See under Schedules |  | DOE Commercial Reference Building TSD and models (V1.3_5.0) and Addendum DF to 90.1-2007
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  | Applicable codes or standards
References
1 | UC Berkeley and LBNL. 2009. LAB21 EnergyPlus Benchmarking Model
2 | PG&E, Southern California Edison, San Diego Gas and Electric Company. 2016. Ultra-Low Temperature Freezers: Opening the Door to Energy Savings in Laboratories, ET14PGE1721
3 | EIA, 2012, Commcer Buildings Energy Consumption Survey (CBECS) 2012
4 | ASHRAE 90.1 2004, 2007, 2010,2013, 2016, Energy Standard for Buildings Except Low-Rise Residential Buildings
5 | ASHRAE 62.1 2004, 2007, 2010, 2013 Ventilation for Acceptable Indoor Air Quality
6 | ASHRAE 62-1999 Ventilation for Acceptable Indoor Air Quality
7 | Labs21. 2008, Laboratory Modeling Guideline using ASHRAE 90.1-2007 Appendix G
8 | Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
9 | PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
10 | PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
11 | Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
12 | Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf
13 | P Mathew, etc. Advanced Benchmarking for Complex Building Types: Laboratories as an Exemplar. ACEEE conference 2010.
14 | DOE. A Guide to Navigating Building and Fire Codes for Laboratories.
15 | National Institutes of Health. Design Requirements Manual. Issued on 12/12/2016, Rev 4/24/2019

## Space Type Summary
Space Type Summary
Floor Function Type | Space Type | Conditioned [Y/N] | Lighting 2 [W/ft²] | People [ft²/person] | Plug and Process [W/ft²] | Cooling Setpoint [F] | Heating Setpoint [F] | Cooling Setback [F] | Heating Setback [F] | Notes
Office | Office | Yes | 1 | 200 | 0.75 | 75 | 70 | 85 | 60
Retail_Standalone | Retail | Yes | 1.7 | 66.6 | 0.3 | 75 | 70 | 85 | 60
Retail_Standalone | Point_of_Sale | Yes | 1.7 | 66.6 | 2 | 75 | 70 | 85 | 60
Retail_Standalone | Back_Space | Yes | 0.839 | 66.6 | 0.7 | 75 | 70 | 85 | 60
Retail_Standalone | Front_Entry | Yes | 1.3 | 66.6 | 0 | 75 | 70 | 85 | 60
Apartment | Apartment | Yes | 1.34 | 380 | 0.62 | 75 | 70 | n/a | n/a | 950ft2
Apartment | Corridor | No | 0.55 | 0 | 0 | 75 | 70 | n/a | n/a
Apartment | Office | Yes | 1.1 | 950 | 0.62 | 75 | 70 | 85 | 60
Hotel | Lobby | Yes | 1.1 | 33.3679 | 0.74973 | 75 | 70 | n/a | n/a
Hotel | Café | Yes | 1.2997 | 14.9617 | 0.49982 | 75 | 70 | n/a | n/a
Hotel | Laundry | Yes | 0.60016 | 100 | 55.53 | 75 | 70 | n/a | n/a
Hotel | Storage | Yes | 0.89931 | 500.6265 | 0.24991 | 75 | 70 | n/a | n/a
Hotel | Occ_Guest_Room_Lg | Yes | 1.1 | 280 | 0.63 | 70 | 70 | n/a | n/a | No setback in 2004, setback 74/66 in 2007+, schedule is different for 2013+
Hotel | Occ_Guest_Room_Sm | Yes | 1.1 | 176 | 0.98 | 70 | 70 | n/a | n/a | No setback in 2004, setback 74/66 in 2007+, schedule is different for 2013+
Hotel | Vac_Guest_Room | Yes | 1.1 | 176 | 0.98 | 74 | 66 | n/a | n/a
Hotel | Corridor | Yes | 0.5 | 997 | 0 | 75 | 70 | n/a | n/a
Hotel | Banquet | Yes | 1.3 | 15 | 6.3 | 75 | 70 | n/a | n/a
Hotel | Dining | Yes | 1.3 | 15 | 6.3 | 75 | 70 | n/a | n/a
Hotel | Kitchen | Yes | 1.1994 | 50 | 272.68 | 75 | 70 | n/a | n/a
All floors | Mechanical | Yes | 1.5 | 0 | 0.5 | 75 | 70 | n/a | n/a | Large Hotel prototype model
Top floor | Elevator_Machine | Yes | 1.5 | 0 | See note | 80 2 | 60 2 | n/a | n/a | Tall: 17*28.3 kW; Super tall: 32*54.5 kW; 15% of heat dissipation
1. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on applicable codes and standards
2. <ASHRAE Design Guide for tall, supertall and megatall building systems> P140

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  | People OSA Ventilation (cfm/person) |  |  |  |  | Area OSA Ventilation (cfm/ft2) |  |  |  |  | Total (combined) OSA Ventilation (cfm/person) |  |  |  |  | Total (combined) OSA Ventilation (cfm/ft2) |  |  |  |  | Exhaust (cfm/zone)
Floor Function Type | Space Type | People [ft²/person] | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2013 (62.1-2010) | 90.1-2016 (62.1-2013) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2013 (62.1-2010) | 90.1-2016 (62.1-2013) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2013 (62.1-2010) | 90.1-2016 (62.1-2013) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2013 (62.1-2010) | 90.1-2016 (62.1-2013) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2013 (62.1-2010) | 90.1-2016 (62.1-2013)
Office | Office | 200 | 20 | 5 | 5 | 5 | 5 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 20 | 17 | 17 | 17 | 17 | 0.1 | 0.085 | 0.085 | 0.085 | 0.085
Retail_Standalone | Retail | 66.6 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 0.3 | 0.12 | 0.12 | 0.12 | 0.12 | 19.98 | 15.492 | 15.492 | 15.492 | 15.492 | 0.3 | 0.23261 | 0.23261 | 0.23261 | 0.23261
Retail_Standalone | Point_of_Sale | 66.6 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 0.3 | 0.12 | 0.12 | 0.12 | 0.12 | 19.98 | 15.492 | 15.492 | 15.492 | 15.492 | 0.3 | 0.23261 | 0.23261 | 0.23261 | 0.23261
Retail_Standalone | Back_Space | 66.6 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12 | 9.99 | 7.992 | 7.992 | 7.992 | 7.992 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12
Retail_Standalone | Front_Entry | 66.6 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 0.3 | 0.12 | 0.12 | 0.12 | 0.12 | 19.98 | 15.492 | 15.492 | 15.492 | 15.492 | 0.3 | 0.23261 | 0.23261 | 0.23261 | 0.23261
Apartment | Apartment | 380 | 15 | 15 | 5 | 5 | 5 | 0 | 0 | 0.06 | 0.06 | 0.06 | 15 | 15 | 27.8 | 27.8 | 27.8 | 0.039474 | 0.039474 | 0.073158 | 0.073158 | 0.073158
Apartment | Corridor | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.06 | 0.06 | 0.06 | 0.06
Apartment | Office | 950 | 20 | 5 | 5 | 5 | 5 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 20 | 62 | 62 | 62 | 62 | 0.021053 | 0.065263 | 0.065263 | 0.065263 | 0.065263
Hotel | Lobby | 33.3679 | 15 | 7.5 | 7.5 | 7.5 | 7.5 | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 15 | 9.5021 | 9.5021 | 9.5021 | 9.5021 | 0.44953 | 0.28477 | 0.28477 | 0.28477 | 0.28477
Hotel | Café | 14.9617 | 20 | 7.5 | 7.5 | 7.5 | 7.5 | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 20 | 10.1931 | 10.1931 | 10.1931 | 10.1931 | 1.3367 | 0.68128 | 0.68128 | 0.68128 | 0.68128
Hotel | Laundry | 100 | 25 | 0 | 5 | 5 | 5 | 0 | 0 | 0.12 | 0.12 | 0.12 | 25 | 0 | 17 | 17 | 17 | 0.25 | 0 | 0.17 | 0.17 | 0.17 | 500 | 500 | 500 | 500 | 500
Hotel | Storage | 500.6265 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12 | 75.094 | 60.0752 | 60.0752 | 60.0752 | 60.0752 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12
Hotel | Occ_Guest_Room_Lg | 280 | 0 | 5 | 5 | 5 | 5 | 0.14286 | 0.06 | 0.06 | 0.06 | 0.06 | 39.9995 | 21.8 | 21.8 | 21.8 | 21.8 | 0.14286 | 0.077857 | 0.077857 | 0.077857 | 0.077857
Hotel | Occ_Guest_Room_Sm | 176 | 0 | 5 | 5 | 5 | 5 | 0.13261 | 0.06 | 0.06 | 0.06 | 0.06 | 23.3396 | 15.56 | 15.56 | 15.56 | 15.56 | 0.13261 | 0.088409 | 0.088409 | 0.088409 | 0.088409
Hotel | Vac_Guest_Room | 176 | 0 | 5 | 5 | 5 | 5 | 0.13261 | 0.06 | 0.06 | 0.06 | 0.06 | 23.3396 | 15.56 | 15.56 | 15.56 | 15.56 | 0.13261 | 0.088409 | 0.088409 | 0.088409 | 0.088409
Hotel | Corridor | 997 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.06 | 0.06 | 0.06 | 0.06 | 49.85 | 59.82 | 59.82 | 59.82 | 59.82 | 0.05 | 0.06 | 0.06 | 0.06 | 0.06
Hotel | Banquet | 15 | 20 | 7.5 | 7.5 | 7.5 | 7.5 | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 20 | 10.2 | 10.2 | 10.2 | 10.2 | 1.3333 | 0.68 | 0.68 | 0.68 | 0.68
Hotel | Dining | 15 | 20 | 7.5 | 7.5 | 7.5 | 7.5 | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 20 | 10.2 | 10.2 | 10.2 | 10.2 | 1.3333 | 0.68 | 0.68 | 0.68 | 0.68
Hotel | Kitchen | 50 | 15 | 0 | 0 | 7.5 | 7.5 | 0 | 0.7 | 0.7 | 0.12 | 0.12 | 15 | 35 | 35 | 13.5 | 13.5 | 0.3 | 0.7 | 0.7 | 0.27 | 0.27 | 4000 | 4000 | 4000 | 4000 | 4000
All floors | Mechanical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Top floor | Elevator_Machine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1. The ventilation requirements are based on the ASHRAE Standard 62.1.
2. The values of cfm/ft2 of hotel guest rooms refer to the DOE Large Hotel Prototype model. Originally, each "Guest Room" zone of 264 sft contains one guestroom with one bedroom and one bath. Each "Guest Room" zone of 420 sft contains one guest suite with one bedroom, one living room, and one bath. ASHRAE 62-1999 requires 30 cfm per each living room and each bedroom and 35 cfm per bath, regardless of area. For bathroom, the 35 cfm OA requirement is the installed capacity for intermittent use. Based on the interpretation from ASHRAE (http://www.ashrae.org/technology/page/913), the 35 cfm of outdoor air can be supplied to the hotel/motel bedroom then exhausted through the bathroom at the same rate, this would meet the standard for both the bedroom and the bathroom. So, we should use a ventilation rate of 35 cfm for guestroom, not 65 cfm. This is consistent with inputs from AEDG Highway Lodging project committee. Thus, the OA rate equals to 35 cfm for standard guest room and 60 cfm for suite.
3. The total kitchen exhaust flow rate is assumed based on engineering judgment and a review of actual kitchen designs (PNNL report: Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010)
4. For hotel kitchen, ventilation requirement is not defined in 62.1-2004 and 2007, only exhaust rate (0.7cfm/fts) is defined, which is used as the ventilation requirement here.
5. The total laundry exhaust flow rate refers to DOE large hotel prototype models.

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Office-Office (applies to all offices)
Source: Large Office prototype model
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Fan Schedule) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
| (°F) |  | SummerDesign | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | Sat | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
|  |  | WinterDesign | 60.08 | 60.08 | 60.08 | 60.08 | 63.68 | 67.28 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
|  |  | Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
CLGSETP_SCH | Temperature | Through 12/31 | WD | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
| (°F) |  | SummerDesign | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | Sat | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | WinterDesign | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
|  |  | Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
Cool-Supply-Air-Temp-Sch | Temperature (°F) | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
Heat-Supply-Air-Temp-Sch | Temperature (°F) | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
CW-Loop-Temp-Schedule | Temperature (°F) | Through 12/31 | All | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06
HW-Loop-Temp-Schedule | Temperature (°F) | Through 12/31 | All | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
MinOA_Sched | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(Climate Zone 1-3) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_MotorizedDamper_Sched | fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Climate Zone 4-8) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retail_Standalone-All space types
Source: Retail Standalone prototype model
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat. | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat. | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
BLDG_EXTERIOR_LIGHT | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(AstronomicalClock control) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
(FAN_SCH) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
| (°C) |  | SummerDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  |  | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
|  |  | Sun, Hol, Other | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
|  |  | WinterDesign | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.04 | 68 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008 | 60.008
| (°F) |  | SummerDesign | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008
|  |  | Sat | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.04 | 68 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008
|  |  | Sun, Hol, Other | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.04 | 68 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008
|  |  | WinterDesign | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 64.994 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 69.998 | 60.008 | 60.008 | 60.008
CLGSETP_SCH | Temperature | Through 12/31 | WD | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
| (°C) |  | WinterDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
|  |  | Sat | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
|  |  | Sun, Hol, Other | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
|  |  | SummerDesign | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
CLGSETP_SCH | Temperature | Through 12/31 | WD | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
| (°F) |  | WinterDesign | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992
|  |  | Sat | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
|  |  | Sun, Hol, Other | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
|  |  | SummerDesign | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 80.006 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 75.002 | 84.992 | 84.992 | 84.992
OA_DAMPER_SCH | on/off | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MinOA_Sched | fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Apartment-Apartment
Source: Highrise Apartment prototype model
People | Fraction | Through 12/31 | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85246 | 0.39344 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.29508 | 0.52459 | 0.86885 | 0.86885 | 0.86885 | 1 | 1 | 1
Lighting | Fraction | Through 12/31 | ALL | 0.011316 | 0.011316 | 0.011316 | 0.011316 | 0.033948 | 0.073554 | 0.079212 | 0.073554 | 0.033948 | 0.022632 | 0.022632 | 0.022632 | 0.022632 | 0.022632 | 0.022632 | 0.039606 | 0.079212 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.067896 | 0.02829
Plug | Fraction | Through 12/31 | ALL | 0.45399 | 0.41104 | 0.39264 | 0.38037 | 0.38037 | 0.42945 | 0.53988 | 0.65031 | 0.66258 | 0.67485 | 0.68712 | 0.69939 | 0.68712 | 0.66258 | 0.65031 | 0.68098 | 0.80368 | 1 | 1 | 0.92638 | 0.88957 | 0.84663 | 0.71166 | 0.57669
Infiltration | Fraction | Through 12/31 | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Cooling | Temperature | Through 12/31 | ALL | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
(°F)
Heating | Temperature | Through 12/31 | ALL | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(°F)
SWH | Fraction | Through 12/31 | ALL | 0.078431 | 0.039216 | 0.0098062 | 0.0098062 | 0.039216 | 0.27451 | 0.94118 | 1 | 0.96078 | 0.84314 | 0.76471 | 0.60784 | 0.52941 | 0.47059 | 0.41176 | 0.47059 | 0.54902 | 0.72549 | 0.86275 | 0.82353 | 0.7451 | 0.60784 | 0.52941 | 0.29412
FAN | Fraction | Through 12/31 | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Apartment-Corridor
Lighting | Fraction | Through 12/31 | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hotel-all below
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
(for public spaces) |  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
|  |  | SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, and Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
(for guest rooms) |  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
|  |  | SummerDesignDay CustomDay1 CustomDay2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
(for public spaces on the ground floor) |  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  |  | SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, and Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
(for guest rooms) |  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  |  | SummerDesignDay CustomDay1 CustomDay2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
(for kitchen, dining and banquet) |  |  | Sat, Sun, Hol, Others | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesignDay | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
(for kitchen) |  |  | Sun, Hol, Others | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  |  | SummerDesignDay | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
(for public spaces) |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
|  |  | SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, and Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
GUESTROOM_ OCC_SCH | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65
(for guest rooms) |  |  | Sat, Sun, Hol, others | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
|  |  | SummerDesignDay CustomDay1 CustomDay2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen_Exhaust_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD,SummerDesignDay | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  | Sat, WinterDesignDay | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  | Sun, Hol, Others | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
|  |  | Others | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Infiltration Schedule
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
(for all zones) |  |  | Sat, Sun, Hol | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Schedules
GUESTROOM_FAN_SCH | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(HVAC Operation)
COMMONAREA_FAN_SCH | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(HVAC Operation)
HtgSetP_Sch | Temperature | Through 12/31 | All | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(°F)
ClgSetP_Sch | Temperature | Through 12/31 | All | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(°F)
MinOA_MotorizedDamper_Sched | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Laundry Exhaust Fan | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.